ENGINEERING SPECIFICATION

50-POINT INTELLIGENT COMMUNICATING FIRE DETECTION SYSTEM

PART 1.0 - GENERAL

1.1. DESCRIPTION:

- This section of the specification includes the furnishing, installation, connection and

testing of the microprocessor controlled, intelligent reporting fire alarm equipment

required to form a complete, operative, coordinated system. It shall include, but not be

limited to, alarm initiating devices, alarm notification appliances, Fire Alarm Control

Panel (FACP), auxiliary control devices, annunciators, and wiring as shown on the

drawings and specified herein.

B. The fire alarm system shall comply with requirements of NFPA Standard No. 72 for Local

Protected Premises Signaling Systems except as modified and supplemented by this

specification. The system field wiring shall be supervised either electrically or by

software-directed polling of field devices.

1. The Secondary Power Source of the fire alarm control panel will be capable of providing

at least 24 hours of backup power with the ability to sustain 5 minutes in alarm at the end

of the backup period.

- The fire alarm system shall be manufactured by an ISO 9001 certified company and meet

the requirements of BS EN9001: ANSI/ASQC Q9001-1994.

D. The FACP and peripheral devices shall be manufactured 100% by a single U.S.

manufacturer (or division thereof).

E. Underwriters Laboratories Inc. (UL) - USA:

UL 38 Manually Actuated Signaling Boxes

UL 217 Smoke Detectors, Single and Multiple Station

UL 228 Door Closers–Holders for Fire Protective Signaling Systems

UL 268 Smoke Detectors for Fire Protective Signaling Systems

UL 268A Smoke Detectors for Duct Applications

UL 346 Waterflow Indicators for Fire Protective Signaling Systems

UL 464 Audible Signaling Appliances

UL 521 Heat Detectors for Fire Protective Signaling Systems

UL 864 Standard for Control Units for Fire Protective Signaling Systems

UL 1481 Power Supplies for Fire Protective Signaling Systems

UL 1610 Central Station Burglar Alarm Units

UL 1638 Visual Signaling Appliances

UL 1971 Signaling Devices for Hearing Impaired

UL 2017 General-Purpose Signaling Devices and System

1. The FACP shall be ANSI 864, 9th Edition Listed.  Systems listed to

ANSI 864, 8th edition (or previous revisions) shall not be accepted.

F. The installing company shall employ NICET (minimum Level II Fire Alarm Technology)

technicians on site to guide the final check-out and to ensure the systems integrity.

1.2. SCOPE:

A. An intelligent, microprocessor-controlled, fire alarm detection system shall be installed in

accordance to the project specifications and drawings.

B. Basic Performance:

1.	Initiation Device Circuits (IDC) shall be wired NFPA Style B (Class B) as part of an

addressable device connected by the SLC Circuit.

2.	When not wired directly from panel NAC circuits, Notification Appliance Circuits

(NAC) shall be wired NFPA Style Y (Class B) as part of an addressable device connected

by the SLC Circuit.

3.	All circuits shall be power-limited, per UL864 requirements.

- A single ground fault or open circuit on the system Signaling Line Circuit shall not cause system malfunction, loss of operating power or the ability to report an alarm.

5.	Alarm signals arriving at the main FACP shall not be lost following a primary power

failure or outage of any kind until the alarm signal is processed and recorded.

6.	Panel shall meet requirements of UL-864 Ninth Edition

C. BASIC SYSTEM FUNCTIONAL OPERATION

When a fire alarm condition is detected and reported by one of the system initiating devices,

the following functions shall immediately occur:

1.	The system Alarm LED on the FACP shall flash.

2.	A local sounder with the control panel shall sound.

3.	A backlit 80-character LCD display on the FACP shall indicate all information associated

with the fire alarm condition, including the type of alarm point and its location within the

protected premises.

4.	In response to a fire alarm condition, the system will process all control programming

and activate all system outputs (alarm notification appliances and/or relays) associated

with the point(s) in alarm

5. In response to a fire alarm condition, the system will process all control

programming and activate all system outputs (alarm notification appliances and/or

relays) associated with the point(s) in alarm.  Additionally, the system shall send

events to a central alarm supervising station via either dial-up over PSTN or

Internet or Intranet via PSDN or virtual private network.

1.3. SUBMITTALS

A. General:

1. Two copies of all submittals shall be submitted to the Architect/Engineer for review.

2.	All references to manufacturer's model numbers and other pertinent information herein is

intended to establish minimum standards of performance, function and quality.

Equivalent compatible UL-listed equipment from other manufacturers may be substituted

for the specified equipment as long as the minimum standards are met.

3.	For equipment other than that specified, the contractor shall supply proof that such

substitute equipment equals or exceeds the features, functions, performance, and quality

of the specified equipment.

B. Shop Drawings:

1.	Sufficient information, clearly presented, shall be included to determine compliance with

drawings and specifications.

2.	Include manufacturer's name(s), model numbers, ratings, power requirements, equipment

layout, device arrangement, complete wiring point-to-point diagrams, and conduit

layouts.

3.	Show annunciator layout, configurations, and terminations.

C. Manuals:

1.	Submit simultaneously with the shop drawings, complete operating and maintenance

manuals listing the manufacturer's name(s), including technical data sheets.

2.	Wiring diagrams shall indicate internal wiring for each device and the interconnections

between the items of equipment.

3.	Provide a clear and concise description of operation that gives, in detail, the information

required to properly operate the equipment and system.

D. Software Modifications

1.	Provide the services of a qualified technician to perform all system software

modifications, upgrades or changes.  Response time of the technician to the site shall not

exceed 4 hours.

2.	Provide all hardware, software, programming tools and documentation necessary to

modify the fire alarm system on site. Modification includes addition and deletion of

devices, circuits, zones and changes to system operation and custom label changes for

devices or zones. The system structure and software shall place no limit on the type or

extent of software modifications on-site. Modification of software shall not require

power-down of the system or loss of system fire protection while modifications are being

made.

1.4. GUARANTY:

All work performed and all material and equipment furnished under this contract shall be

free from defects and shall remain so for a period of at least one (1) year from the date of

acceptance. The full cost of maintenance, labor and materials required to correct any defect

during this one year period shall be included in the submittal bid.

1.5. MAINTENANCE:

A. Maintenance and testing shall be on a semi-annual schedule or as required by the local

AHJ. A preventive maintenance schedule shall be provided by the contractor describing

the protocol for preventive maintenance. The schedule shall include:

1. Systematic examination, adjustment and cleaning of all detectors, manual fire alarm

stations, control panels, power supplies, relays, waterflow switches and all accessories

of the fire alarm system.

2. Each circuit in the fire alarm system shall be tested semiannually.

3. Each smoke detector shall be tested in accordance with the requirements of NFPA 72

Chapter 10.

B. As part of the bid/proposal, include a quote for a maintenance contract to provide all

maintenance, tests, and repairs described below. Include also a quote for unscheduled

maintenance/repairs, including hourly rates for technicians trained on this equipment, and

response travel costs for each year of the maintenance period. Submittals that do not

identify all post contract maintenance costs will not be accepted. Rates and costs shall be

valid for the period of five (5) years after expiration of the guaranty.

1.6. POST CONTRACT EXPANSIONS:

A. The contractor shall have the ability to provide parts and labor to expand the system

specified, if so requested, for a period of five (5) years from the date of acceptance.

B. As part of the submittal, include a quotation for all parts and material, and all installation

and test labor as needed to increase the number of intelligent or addressable devices by ten

percent (10%). This quotation shall include intelligent smoke detectors, intelligent heat

detectors, addressable manual stations, addressable beam detectors, addressable monitor

modules and addressable control modules equal in number to one tenth of the number

required to meet this specification (list actual quantity of each type).

C. The quotation shall include installation, test labor, and labor to reprogram the system for

this 10% expansion. If additional FACP hardware is required, include the material and

labor necessary to install this hardware.

D. Do not include cost of conduit or wire or the cost to install conduit or wire except for labor

to make final connections at the FACP and at each intelligent addressable device. Do not

include the cost of conventional peripherals or the cost of initiating devices or notification

appliances connected to the addressable monitor/control modules.

E. Submittals that do not include this estimate of post contract expansion cost will not be

accepted.

1.7. APPLICABLE STANDARDS AND SPECIFICATIONS:

The specifications and standards listed below form a part of this specification. The system shall fully comply with the latest issue of these standards, if applicable.

A. National Fire Protection Association (NFPA) - USA:

No. 13	Sprinkler Systems

No. 70	National Electric Code (NEC)

No. 72	National Fire Alarm Code

No. 101 Life Safety Code

B. The system and its components shall be Underwriters Laboratories, Inc. listed under the

appropriate UL testing standard as listed herein for fire alarm applications and the

installation shall be in compliance with the UL listing.

C. Local and State Building Codes.

D. All requirements of the Authority Having Jurisdiction (AHJ).

1.8. APPROVALS:

A. The system shall have proper listing and/or approval from the following nationally

recognized agencies:

UL	Underwriters Laboratories Inc (Ninth Edition)

FM	Factory Mutual

MEA	Material Equipment Acceptance (NYC)

CSFM	California State Fire Marshal

CAN/ULC - S527-99 Standard for Control Units for Fire Alarm Systems

PART 2.0 PRODUCTS

2.1. EQUIPMENT AND MATERIAL, GENERAL:

A. All equipment and components shall be new, and the manufacturer's current model. The

materials, appliances, equipment and devices shall be tested and listed by a nationally

recognized approvals agency for use as part of a fire protective signaling system, meeting

the National Fire Alarm Code.

B. All equipment and components shall be installed in strict compliance with manufacturers'

recommendations. Consult the manufacturer's installation manuals for all wiring diagrams,

schematics, physical equipment sizes, etc., before beginning system installation.

C. All equipment shall be attached to walls and ceiling/floor assemblies and shall be held

firmly in place (e.g., detectors shall not be supported solely by suspended ceilings).

Fasteners and supports shall be adequate to support the required load.

D. All equipment must be available "over the counter" through the Security Equipment

Distributor (SED) market and can be installed by dealerships independent of the

manufacturer.

2.2. CONDUIT AND WIRE:

A. Conduit:

1.	Conduit shall be in accordance with The National Electrical Code (NEC), local and state

requirements.

2. Where required, all wiring shall be installed in conduit or raceway.  Conduit fill shall not

exceed 40 percent of interior cross sectional area where three or more cables are contained

within a single conduit.

3.	Cable must be separated from any open conductors of power, or Class 1 circuits, and shall not be placed

in any conduit, junction box or raceway containing these conductors, per NEC Article 760-29.

4.	With the exception of telephone connections, wiring for 24 volt DC control, alarm

notification, emergency communication and similar power-limited auxiliary functions

may be run in the same conduit as initiating and signaling line circuits. All circuits shall

be provided with transient suppression devices and the system shall be designed to permit

simultaneous operation of all circuits without interference or loss of signals.

5.	Conduit shall not enter the fire alarm control panel, or any other remotely mounted

control panel equipment or backboxes, except where conduit entry is specified by the

FACP manufacturer.

6.	Conduit shall be 3/4 inch (19.1 mm) minimum.

B. Wire:

1.	All fire alarm system wiring shall be new.

2.	Wiring shall be in accordance with local, state and national codes (e.g., NEC Article 760)

and as recommended by the manufacturer of the fire alarm system. Number and size of

conductors shall be as recommended by the fire alarm system manufacturer, but not less

than 18 AWG (1.02 mm) for Initiating Device Circuits and Signaling Line Circuits, and

14 AWG (1.63 mm) for Notification Appliance Circuits.

3.	All wire and cable shall be listed and/or approved by a recognized testing agency for use

with a protective signaling system.

4.	Wire and cable not installed in conduit shall have a fire resistance rating suitable for the

installation as indicated in NEC 760 (e.g., FPLR).

5.	Wiring used for the multiplex communication circuit (SLC) shall be twisted non-shielded

and support a minimum wiring distance of 10,000 feet when sized at 12 AWG.

6. All field wiring shall be electrically supervised for open circuit and ground fault.

7. The fire alarm control panel shall be capable of T-tapping NFPA Style 4 (Class B)

Signaling Line Circuits (SLCs). Systems which do not allow or have restrictions for the

number of T-taps, length of T-taps etc., are not acceptable.

C. Terminal Boxes, Junction Boxes and Cabinets:

All boxes and cabinets shall be UL listed for their use and purpose.

D. The fire alarm control panel shall be connected to a separate dedicated branch circuit,

maximum 20 amperes. This circuit shall be labeled at the main power distribution panel as

FIRE ALARM. Fire alarm control panel primary power wiring shall be 12 AWG. The

control panel cabinet shall be grounded securely to either a cold water pipe or grounding

rod.  The control panel enclosure shall feature a quick removal chassis to facilitate rapid

replacement of the FACP electronics.

1. The FACP shall be capable of coding Notification Appliance Circuits in March Time

Code (120 PPM), Temporal (NFPA 72 A-2-2.2.2), and California Code. Main panel

notification circuits (NACs 1 & 2) shall also automatically synchronize any of the

following manufacturer’s notification appliances connected to them: System Sensor,

Wheelock, and Gentex, with no need for additional synchronization modules.

2.3. MAIN FIRE ALARM CONTROL PANEL:

A. The FACP shall be a Fire-Lite Model MS-9050UD and shall contain a microprocessor-

based Central Processing Unit (CPU). The CPU shall communicate with and control the

following types of equipment used to make up the system: intelligent addressable smoke

and thermal (heat) detectors, addressable modules, printer, annunciators, Digital Dialer and

Ethernet Communicators and other system controlled devices. Ethernet communications

shall be via a Fire-Lite Model IPDACT.  Central station supervisory equipment shall be a

Teldat Corporation Visoralarm-Plus 2U listed to UL-864 standards.

B. Operator Control

1.	Acknowledge Switch:

a. Activation of the control panel Acknowledge switch in response to new alarms and/or

troubles shall silence the local panel piezo electric signal and change the alarm and

trouble LEDs from flashing mode to steady-ON mode. If multiple alarm or trouble

conditions exist, depression of this switch shall advance the 80-character LCD display

to the next alarm or trouble condition.

b. Depression of the Acknowledge switch shall also silence all remote annunciator piezo

sounders.

2.	Alarm Silence Switch:

Activation of the alarm silence switch shall cause all programmed alarm notification

appliances and relays to return to the normal condition after an alarm condition. The

selection of notification circuits and relays that are silence able by this switch shall be

fully field programmable within the confines of all applicable standards. The FACP

software shall include silence inhibit and auto-silence timers.

3.	Alarm Activate (Drill) Switch:

The Alarm Activate switch shall activate all notification appliance circuits. The drill

function shall latch until the panel is silenced or reset.

4.	System Reset Switch:

Activation of the System Reset switch shall cause all electronically-latched initiating

devices, appliances or software zones, as well as all associated output devices and

circuits, to return to their normal condition.

5.	Lamp Test:

The System RESET switch shall also function as a Lamp Test switch and shall activate

all system LEDs and light each segment of the liquid crystal display.

C. System Capacity and General Operation

1. The control panel shall provide, or be capable of, expansion to 50 intelligent/addressable

devices of any type, detector or module

2. The control panel shall include two Form-C programmable relays, which can be used

for Alarm, and Supervisory and a fixed Trouble relay rated at a minimum of 2.5 amps

@ 30 VDC. It shall also include 2 programmable Notification Appliance Circuits

(NACs) capable of being wired as NFPA Style Y (Class B) or NFPA Style Z (Class A).

Either programmable Notification circuit shall also be capable of providing auxiliary

power when programmed as such.

3. The fire alarm control panel shall include an operator interface control and annunciation

panel that shall include a backlit Liquid Crystal Display (LCD), individual color-coded

system status LEDs, and an alphanumeric keypad for the field programming and control

of the fire alarm system.

4. All programming or editing of the existing program in the system shall be achieved

without special equipment and without interrupting the alarm monitoring functions of

the fire alarm control panel. The system shall be fully programmable, configurable, and

expandable in the field without the need for special tools, PROM programmers or PC

based programmers. It shall not require replacement of memory ICs to facilitate

programming changes.  The control unit will support the ability to upgrade its operating

program using FLASH memory technology.  The unit shall provide the user with the

ability to program from either the included keypad, a standard PS2-style PC keyboard or

from a computer running upload/download software.

5. The system shall allow the programming of any input to activate any output or group of

outputs. Systems which have limited programming (such as general alarm), have

complicated programming (such as a diode matrix), or REQUIRE a laptop personal

computer are not considered suitable substitutes.

6. The FACP shall provide the following features:

a. Drift compensation to extend detector accuracy over life. Drift compensation shall also

include a smoothing feature, allowing transient noise signals to be filtered out.

b. Detector sensitivity test, meeting requirements of NFPA 72, Maintenance alert, with

two levels (maintenance alert/maintenance urgent), to warn of excessive smoke

detector dirt or dust accumulation.

c. The ability to display or print system reports.

d. Alarm verification, with counters and a trouble indication to alert maintenance

personnel when a detector enters verification an excessive number of times.

e. Positive Alarm Sequence (PAS presignal), meeting NFPA 72  requirements.

f. Rapid manual station reporting.

g. Non-alarm points for general (non-fire) control.

h. Periodic detector test, conducted automatically by the software.

i. Walk test, with a check for two detectors set to same address.

7. The FACP shall be capable of coding Notification Appliance Circuits in March Time

Code (120 PPM), Temporal (NFPA 72 ), and California Code. Main panel notification

circuits (NACs 1 & 2) shall also automatically synchronize and be programmable for any

of the following manufacturer’s notification appliances connected to them: System

Sensor, Wheelock, Gentex, with no need for additional synchronization modules

B. Central Microprocessor

1. The microprocessor shall be a state-of-the-art; high speed, 16-bit RISC device and it

shall communicate with, monitor and control all external interfaces. It shall include an

EPROM for system program storage, non-volatile memory for building-specific

program storage, and a "watch dog" timer circuit to detect and report microprocessor

failure.

2. The microprocessor shall contain and execute all specific actions to be taken in the

condition of an alarm. Control programming shall be held in non-volatile programmable

memory, and shall not be lost even if system primary and secondary power failure

occurs.

3. The microprocessor shall also provide a real-time clock for time annotation of system

displays, printer, and history file.

4. A special program check function shall be provided to detect common operator errors.

5. An auto-programming capability (self-learn) shall be provided to quickly identify

devices connected on the SLC and make the system operational.

6. For flexibility and to ensure program validity, an optional Windows(TM) based program

utility shall be available. This program shall be used to off-line program the system with

batch upload/download. This program shall also have a verification utility which scans

the program files, identifying possible errors. It shall also have the ability to compare

old program files to new ones, identifying differences in the two files to allow complete

testing of any system operating changes. This shall be in incompliance with the NFPA

72 requirements for testing after system modification.

C. Local Keyboard Interface

1. In addition to an integral keypad, the fire alarm control panel will accept a standard

PS2-style keyboard for programming, testing, and control of the system. The keyboard

will be able to execute the system functions ACKNOWLEDGE, SIGNALS

SILENCED, DRILL and RESET.

D. Display

1. The display shall provide all the controls and indicators used by the system operator and

may also be used to program all system operational parameters.

2. The display shall include status information and custom alphanumeric labels for all

intelligent detectors, addressable modules, internal panel circuits, and software zones.

3. The display shall contain an alphanumeric, text-type display and dedicated LEDs for the

annunciation of AC POWER, FIRE ALARM, SUPERVISORY, TROUBLE, , and

ALARM SILENCED, , , conditions.

4. The display keypad shall be part of the standard system and have the capability to

command all system functions, entry of any alphabetic or numeric information, and field

programming. Two different password levels shall be provided to prevent unauthorized

system control or programming.

5. The display shall include the following operator control switches:

ACKNOWLEDGE/STEP, ALARM SILENCE, DRILL (alarm activate), and SYSTEM

RESET.

E. Signaling Line Circuit (SLC)

1. The SLC interface shall provide power to and communicate with up to 50 devices of

any type including: intelligent detectors (ionization, photoelectric or thermal)

addressable pull stations, addressable Beam Detectors, intelligent modules (monitor or

control). Each SLC shall be capable of NFPA 72 Style 4, Style 6, or Style 7 (Class A or

B) wiring.

2. The CPU shall receive information from all intelligent detectors to be processed to

determine whether normal, alarm, pre-alarm, or trouble conditions exist for each

detector. The software shall automatically compensate for the accumulation of dust in

each detector up to allowable limits. The information shall also be used for automatic

detector testing and for the determination of detector maintenance conditions.

3. The detector software shall meet NFPA 72, Chapter 10 requirements and be certified by

UL as a calibrated sensitivity test instrument.

F. Serial Interfaces

1. An annunciator RS-485 bus shall be used to connect an UL-Listed 80-column printer

anywhere within the 6,000 range of the serial bus connection. The printer shall

communicate with the control panel using an RS-485 converter/interface complying

with Electrical Industries Association standard EIA-232D. Power to the printer shall be

120 VAC @ 60 Hz.  The interface shall contain both a 9-pin serial and standard

centronics parallel connector.  Either shall be capable of connection to a serial or

parallel printer.  The bus shall also provide connection to additional addressable

modules supporting remote 80 character LCD text annunciators that mimic the standard

panel display and controls.  Said annunciators shall support remote acknowledge,

silence, drill and reset functions and shall be enabled via a keyswitch.  The bus shall

also provide connection to addressable modules supporting up to 40 LEDs for use with a

graphic annunciator.

G. The control panel will have the capability of Reverse Polarity Transmission or connection

to a Municipal Box for compliance with applicable NFPA standards.

H. Digital Alarm Communicator Transmitter (DACT) and Internet Protocol Digital

Alarm Communicator Transmitter (IPDACT). The DACT is an interface for

communicating digital information between a fire alarm control panel and a UL-

Listed central station. When the optional IPDACT Ethernet module is connected to

the on board DACT, the system shall be capable of transmitting contact ID

formatted alarms to a central station equipped with a compatible IP receiver via

Ethernet over a private or public WAN/LAN, Intranet or Ethernet

1. The IPDACT communicator shall be an integral module component of the fire

alarm control panel enclosure.

2. The IPDACT communicator shall include connections to the alarm panel’s

phone outputs and shall convert the contact ID protocol in DTMF form into

UDP Ethernet Packets. It shall include the ability for simultaneous reporting of

panel events up to three different IP addresses.

3. The IPDACT communicator shall be completely field-programmable locally

from a PC via a serial port or via Ethernet and Telnet.

4. The IPDACT communicator shall be capable of transmitting events in contact

ID format.

5. Communication shall include vital system status such as:

-	Independent Zone (Alarm, trouble, non-alarm, supervisory)

-	Independent Addressable Device Status

-	AC (Mains) Power Loss

-	Low Battery and Earth Fault

-	System Off Normal

-	12 and 24 Hour Test Signal

-	Abnormal Test Signal (per UL requirements)

-	EIA-485 Communications Failure

-	IP Line Failure

6. The IPDACT communicator shall support independent zone/point reporting via

the Contact ID format. In this format, the IPDACT shall support the transmission

of addressable points within the system. This format shall enable the central

station to have exact details concerning the location of the fire for emergency

response.  The IPDACT communicator shall be capable of providing simulated

phone lines to the FACP and panel communication over IP shall be transparent

to the panels normal operation over phone lines.

7. The IPDACT communicator shall utilize a supervisory heart beat signal of no

less than once every 90 seconds insuring multiplexed level line supervision.

Loss of Internet or Intranet connectivity shall be reported in no more than 200

seconds.

Alarm events shall be transmitted to a central station in no less than 90

seconds from time of initiation to time of notification.

8. The supervising station shall consist of a Teldat Corporation Visoralarm-Plus 2U

receiver.  Said receiver shall contain a smart card for backup of all account data.

Backup smart card shall initiate a new receiver with all account information in

Less than 60 seconds from power up.

I. Enclosures:

1. The control panel shall be housed in a UL-listed cabinet suitable for surface or semi-

flush mounting. The cabinet and front shall be corrosion protected and painted red via

the powder coat method with manufacturer's standard finish.

2. The back box and door shall be constructed of steel with provisions for electrical

conduit connections into the sides and top.

3. The door shall provide a key lock and shall provide for the viewing of all indicators.

4. The cabinet shall accept a chassis containing the PCB and to assist in quick replacement

of all the electronics including power supply shall require no more than two bolts to

secure the panel to the enclosure back box.

5. The cabinet shall also support a mechanical secured optional dress panel limiting access

to the internals of the panel.

J. Field Charging Power Supply:

The FCPS is a device designed for use as either a remote 24-volt power supply or as a

booster for powering Notification Appliances.

1.	The FCPS shall offer up to 8.0 amps (6.0 amps continuous) of regulated 24 volt power. It

shall include an integral charger designed to charge 18.0 amp hour batteries.

2.	The Field Charging Power Supply shall have two input triggers. The input trigger shall be

a Notification Appliance Circuit (from the fire alarm control panel) or a control relay.

Four NAC outputs, wired NFPA Style Y or Z, shall be available for connection to the

Notification devices.

3.	The FCPS shall optionally provide synchronization of all connected strobes or horn

strobe combinations when System Sensor, Wheelock or Gentex devices are installed.

- The FCPS shall function as a sync follower as well as a sync generator.

5.	The FCPS shall include a surface mount backbox.

6.	The Field Charging Power Supply shall include the ability to delay the reporting of an

AC fail condition per NFPA requirements.

- The FCPS shall provide 24 VDC regulated and power-limited circuitry per  UL

standards.  Should this be updated to latest UL standard?

K. Power Supply:

1. The main power supply for the fire alarm control panel shall provide up to 3.0 amps of

available power for the control panel and peripheral devices.

2. Provisions will be made to allow the audio-visual power to be increased as required by

adding modular expansion audio-visual power supplies.

3. Positive-Temperature-Coefficient (PTC) thermistors, circuit breakers, or other over-

current protection shall be provided on all power outputs. The power supply shall

provide an integral battery charger or may be used with an external battery and charger

systems. Battery arrangement may be configured in the field.

4. The main power supply shall continuously monitor all field wires for earth ground

conditions.

5. The main power supply shall operate on 120 VAC, 60 Hz, and shall provide all

necessary power for the FACP.

L. Programmable Electronic Sounders:

1. Electronic sounders shall operate on 24 VDC nominal.

2. Electronic sounders shall be field programmable without the use of special tools, to

provide slow whoop, continuous, or interrupted tones with an output sound level of at

least 90 dBA measured at 10 feet from the device.

3. Electronic sounders shall be flush or surface mounted as shown on plans.

M. Strobe lights shall meet the requirements of the ADA, UL Standard 1971 and shall meet

the following criteria:

1. The maximum pulse duration shall be 2/10 of one second.

2. Strobe intensity shall meet the requirements of UL 1971.

3. The flash rate shall meet the requirements of UL 1971.

N. Audible/Visual Combination Devices:

1. Shall meet the applicable requirements of Section A listed above for audibility.

2. Shall meet the requirements of Section B listed above for visibility.

O.	Specific System Operations

1. Alarm Verification: Each of the intelligent addressable smoke detectors in the system

may be independently programmed for verification of alarm signals. The alarm

verification time period shall not exceed 2 minutes.

2. Point Disable: Any addressable device or conventional circuit in the system may be

enabled or disabled through the system keypad.

3. Point Read: The system shall be able to display the following point status diagnostic

functions:

a.	Device status

b.	Device type

c.	Custom device label

d.	Device zone assignments

4. System Status Reports: Upon command from an operator of the system, a status report

will be generated and printed, listing all system status.

5. System History Recording and Reporting: The fire alarm control panel shall contain a

history buffer that will be capable of storing up to 500 events. Each of these activations

will be stored and time and date stamped with the actual time of the activation. The

contents of the history buffer may be manually reviewed, one event at a time, or

printed in its entirety.

The history buffer shall use non-volatile memory. Systems that use volatile memory

for history storage are not acceptable substitutes.

6. Automatic Detector Maintenance Alert: The fire alarm control panel shall automatically interrogate each intelligent detector and shall analyze the detector responses over a period of time. If any intelligent detector in the system responds with a reading that is above or below normal limits, then the system will enter the trouble mode, and the particular detector will be annunciated on the system display.  This feature shall in no way inhibit the receipt of alarm conditions in the system, nor shall it require any special hardware, special tools or computer expertise to perform.

7. Pre-Alarm Function: The system shall provide two levels of pre-alarm warning to give

advance notice of a possible fire situation. Both pre-alarm levels shall be fully field

adjustable. The first level shall give an audible indication at the panel. The second

level shall give an audible indication and may also activate control relays. The system

shall also have the ability to activate local detector sounder bases at the pre-alarm

level, to assist in avoiding nuisance alarms.

8. The fire alarm control panel shall include Silent and Audible Walk Test functions –

Silent and Audible. It shall include the ability to test initiating device circuits and

Notification Appliance Circuits from the field without returning to the panel to reset the

system. The operation shall be as follows:

a. The Silent Walk Test will not sound NACs but will store the Walk Test information

in History for later viewing.

b. Alarming an initiating device shall activate programmed outputs, which are selected

to participate in Walk Test.

c. Introducing a trouble into the initiating device shall activate the programmed outputs.

d. Walk Test shall be selectable on a per device/circuit basis. All devices and circuits

which are not selected for Walk Test shall continue to provide fire protection and if

an alarm is detected, will exit Walk Test and activate all programmed alarm

functions.

e. All devices tested in walk test shall be recorded in the history buffer.

9. Waterflow Operation: An alarm from a waterflow detection device shall activate the

appropriate alarm message on the control panel display; turn on all programmed

Notification Appliance Circuits and shall not be affected by the Signal Silence switch.

10. Supervisory Operation: An alarm from a supervisory device shall cause the appropriate

indication on the control panel display, light a common supervisory LED, but will not

cause the system to enter the trouble mode.

11. Signal Silence Operation: The FACP shall have the ability to program each output

circuit (notification circuit or relay) to deactivate upon depression of the Signal Silence

switch.

12. Non-Alarm Input Operation: Any addressable initiating device in the system may be

used as a non-alarm input to monitor normally open contact type devices. Non-alarm

functions are a lower priority than fire alarm initiating devices.

1.9. SYSTEM COMPONENTS:

A. Addressable Pull Box (manual station)

1.	Addressable pull boxes shall, on command from the control panel, send data to the panel

representing the state of the manual switch and the addressable communication module

status. They shall use a key operated test-reset lock, and shall be designed so that after

actual emergency operation, they cannot be restored to normal use except by the use of a

key.

2.	All operated stations shall have a positive, visual indication of operation and utilize a key

type reset.

3.	Manual pull stations shall be constructed of Lexan with clearly visible operating

instructions provided on the cover. The word FIRE shall appear on the front of the

stations in raised letters, 1.75 inches (44 mm) or larger.

B. Intelligent Multi-Sensing Detector

1.	The intelligent detector shall be an addressable device which is capable of detecting

multiple threats by employing photoelectric and thermal technologies in a single unit.

This detector shall utilize advanced electronics which react to slow smoldering fires

(photoelectric) and heat (thermal) all within a single sensing device.

2.	The multi-detector shall include two bicolor LEDs for 360-degree viewing.

3. Automatically adjusts sensitivity levels without the need for operator intervention or

programming. Sensitivity increases with heat.

C. Intelligent Photoelectric Smoke Detector

1.	The detectors shall use the photoelectric (light-scattering) principal to measure smoke

density and shall, on command from the control panel, send data to the panel representing

the analog level of smoke density.

2. The detectors shall be ceiling-mounted and available in an alternate model with an

integral fixed 135-degree heat-sensing element.

3. Each detector shall contain a remote LED output and a built-in test switch.

4. Detector shall be provided on a twist-lock base.

5. It shall be possible to perform a calibrated sensitivity and performance test on the

detector without the need for the generation of smoke.  The test method shall test all

detector circuits.

6.	A visual indication of an alarm shall be provided by dual latching Light Emitting Diodes

(LEDs), on the detector, which may be seen from ground level over 360 degrees. These

LEDs shall periodically flash to indicate that the detector is in communication with the

control panel.

7.	The detector shall not go into alarm when exposed to air velocities of up to 1500 feet per

minute (fpm).

8.	The detector screen and cover assembly shall be easily removable for field cleaning of

the detector chamber.

9. All field wire connections shall be made to the base through the use of a clamping plate

and screw.

E. Projected Addressable Beam Detector

1. The projected beam type shall be a 4-wire 24 VDC intelligent, addressable projected

beam smoke detector device.

2. The detector shall be listed to UL 268 and shall consist of a single transmitter\receiver

and corresponding non powered reflector.

3. The detector shall operate in either a short range (16' - 230') or long range (16' - 328')

when used with an extender module.

4.	The temperature range of the device shall be -22 degrees F to 131 degrees

5. The detector shall feature an optical sight and 2-digit signal strength meter to ensure

proper alignment of unit without need of special tools.

6. The unit shall be both ceiling and wall mountable.

7. The detector shall have the ability to be tested using calibrated test filters or magnet-

activated remote test station.}

8. The detector shall have four standard sensitivity selections along with two automatic self-

adjusting settings. When either of the two automatic settings is selected the detector will

automatically adjust its sensitivity using advanced software algorithms to select the

optimum sensitivity for the specific environment.

F. Intelligent Ionization Smoke Detector

1.	The detectors shall use the dual-chamber ionization principal to measure products of

combustion and shall, on command from the control panel, send data to the panel

representing the analog level of products of combustion.

G. Intelligent Thermal Detectors

1. Thermal detectors shall be intelligent addressable devices rated at 135 degrees Fahrenheit

(58 degrees Celsius) and have a rate-of-rise element rated at 15 degrees F (9.4 degrees C)

per minute. It shall connect via two wires to the fire alarm control panel signaling line

circuit.

H. Intelligent Duct Smoke Detector

1. The smoke detector housing shall accommodate either an intelligent ionization detector

or an intelligent photoelectric detector, of that provides continuous analog monitoring

and alarm verification from the panel.

2. When sufficient smoke is sensed, an alarm signal is initiated at the FACP, and

appropriate action taken to change over air handling systems to help prevent the rapid

distribution of toxic smoke and fire gases throughout the areas served by the duct

system.

I. Addressable Dry Contact Monitor Module

1.	Addressable monitor modules shall be provided to connect one supervised IDC zone of

conventional alarm initiating devices (any normally open dry contact device) to one of

the fire alarm control panel SLCs.

2.	The monitor module shall mount in a 4-inch square (101.6 mm square), 2-1/8 inch (54

mm) deep electrical box.

3.	The IDC zone shall be suitable for Style D or Style B operation. An LED shall be

provided that shall flash under normal conditions, indicating that the monitor module is

operational and in regular communication with the control panel.

4.	For difficult to reach areas, the monitor module shall be available in a miniature package

and shall be no larger than 2-3/4 inch (70 mm) x 1-1/4 inch (31.7 mm) x 1/2 inch (12.7

mm). This version need not include Style D or an LED.

J. Two-Wire Detector Monitoring

1.	Means shall be provided for the monitoring of conventional Initiating Device Circuits

populated with 2-wire smoke detectors as well as normally-open contact alarm initiating

devices (pull stations, heat detectors, etc).

2.	Each IDC of conventional devices will be monitored as a distinct address on the polling

circuit by an addressable module.  The module will supervise the IDC for alarms and

circuit integrity (opens).

3.	The monitoring module will be compatible, and listed as such, with all devices on the

supervised circuit.

4.	The IDC zone may be wired for Style D or Style B (Class A or B) operation. An LED

shall be provided that shall flash under normal conditions, indicating that the monitor

module is operational and in regular communication with the control panel.

5.	The monitoring module shall be capable of mounting in a 4-inch square (101.6 mm

square), 2-1/8 inch (54 mm) deep electrical box or in an surface mount backbox.

K. Addressable Control Relay Module

1.	Addressable control relay modules shall be provided to control the operation of fan

shutdown and other auxiliary control functions.

2.	The control module shall mount in a standard 4-inch square, 2-1/8 inch deep electrical

box, or to a surface mounted backbox.

3.	The control relay module will provide a dry contact, Form-C relay. The relay coil shall be

magnetically latched to reduce wiring connection requirements, and to insure that 100%

of all auxiliary relays may be energized at the same time on the same pair of wires.

4.	The control relay module shall be suitable for pilot duty applications and rated for a

minimum of 0.6 amps at 30 VDC.

L. Six Output Addressable Control Relay Module

1.	Up to 6 Addressable intelligent control relay modules combined on one circuit board

shall be provided to control the operation of fan shutdown and other auxiliary control

functions.

2.	Using rotary address switches, the first module shall be addressed from 01 to 45 while

the remaining modules shall be automatically assigned to the next five higher addresses.

Note, binary dip switches for setting address are not acceptable.

3.	Provision shall be included for disabling a maximum of three unused modules

4.	A single isolated set of dry relay form C contacts shall be provided for each of the 6

module addresses, which shall be capable of being wired for either a normally-open or

normally-closed operation.

5.	The module shall allow an addressable control panel to switch these contacts on

command.

6.	The module shall contain removable plug in terminal blocks capable of supporting 12

AWG to 18 AWG wire.

7.	The control relays mounted on the module shall be suitable for pilot duty applications and

rated for a maximum of 3.0 amps at 30 VDC, resistive, non-coded and 2.0 amps at 30

VDC maximum, resistive, coded.

M. Six-Zone Interface Module

1.	A six zone interface module shall be provided as an interface between the addressable

panel and two-wire conventional detection zones.

2.	A common SLC input shall be used for all modules, and the initiating device circuits

shall share a common external supervisory supply and ground.

3.	The first address on the interface module shall be addressed from 01 to 45 while the

remaining modules are automatically assigned to the next five higher addresses.

4.	Address shall be set using decimal encoded rotary address switches.  Binary address

switches are not acceptable.

5.	Provision shall be included for disabling a maximum of two unused addresses of the six

available.

6.	All two-wire detectors being monitored shall be two-wire compatibility listed with the six

zone input module.

7.	The six zone input module shall transmit the status of a zone of two-wire detectors to the

fire alarm control panel.  Status shall be reported as normal, open or alarm.

8.	Removable plug-in terminals shall be provided capable of accepting from 18 AWG up to

12 AWG wire.

N. Multiple Two-Wire Detector Monitoring

1.	A single multi input module shall be provided for the monitoring of up to 10

conventional Initiating Device Circuits populated with 2-wire smoke detectors as well as

normally-open contact alarm initiating devices (pull stations, heat detectors, etc).

2.	Each IDC of conventional devices will be monitored as a distinct address on the polling

circuit by an addressable point.  The module will supervise the IDC for alarms and circuit

integrity (opens).

3.	The first address on the 10 input boards shall be set from 01 to 40 and the remaining

module addresses shall be automatically assigned to the next nine higher addresses.

4.	Provision shall be included for disabling a maximum of two unused addresses.

5.	The supervised state (normal, open, or short) of the monitored device shall be sent back

to the panel.  A common SLC input shall be used for all modules, and the initiating

device loops shall share a common supervisory supply and ground.

6.	The IDC zone may be wired for Style D or Style B (Class A or B) operation. A green

LED for each circuit shall be provided that shall flash under normal conditions, indicating

that the monitor module is operational and in regular communication with the control

panel.  LEDs shall latch on when a circuit is in alarm.

O. Isolator Module

1.	Isolator modules shall be provided to automatically isolate wire-to-wire short circuits on

an SLC Style 6 (Class A) or Style 4 (Class B branch). The isolator module shall limit the

number of modules or detectors that may be rendered inoperative by a short circuit fault

on the SLC loop segment or branch. At least one isolator module shall be provided for

each floor or protected zone of the building.

2.	If a wire-to-wire short occurs, the isolator module shall automatically open-circuit

(disconnect) the SLC. When the short circuit condition is corrected, the isolator module

shall automatically reconnect the isolated section.

3.	The isolator module shall not require any address-setting, and its operations shall be

totally automatic. It shall not be necessary to replace or reset an isolator module after its

normal operation.

4.	The isolator module shall mount in a standard 4-inch (101.6 mm) deep electrical box or

in a surface mounted backbox. It shall provide a single LED that shall flash to indicate

that the isolator is operational and shall illuminate steadily to indicate that a short circuit

condition has been detected and isolated.

P. Serially Connected Graphic LED driver module

1. An LED driver module shall communicate with the fire alarm control panel via a two

wire EIA 485 (multi-drop) communications circuit.

2. The annunciator shall require no more than two wires for operation and two wires for

power. Annunciation shall include Outputs for up to 40 LEDs.

a. Up to 8 total devices of any kind, LCD, printer gateway, LED, Relay or I/O module

may be installed on the ANN-BUS.

Q. Alphanumeric LCD Type Annunciator:

1. The alphanumeric display annunciator shall be a supervised, remotely located back-lit

eighty (80) characters LCD display for alarm annunciation in clear English text.

2. The LCD annunciator shall display all alarm and trouble conditions in the system.

3. An audible indication of alarm shall be integral to the alphanumeric display.

4. The display shall be UL listed for fire alarm application.

5. It shall be possible to connect up to 8 LCD displays and be capable of wiring distances

up to 6,000 feet from the control panel.

6. The annunciator shall connect to a separate, dedicated "terminal mode" EIA-RS-485

interface using two-wire loop connection and 2 wires for power. Each terminal mode

LCD display shall mimic the main control panel.

R. Field Wiring Terminal Blocks

For ease of connection for heavy solid gage wire, all panel I/O wiring terminal blocks shall

be screw type barrier strips and have sufficient capacity for #18 to #12 AWG wire.

1.10. SYSTEM COMPONENTS - ADDRESSABLE DEVICES

A. Addressable Devices - General

1. Addressable devices shall employ the simple-to-set decade addressing scheme.

Addressable devices which use a binary-coded address setting method, such as a DIP

switch, are not an allowable substitute.

2. Detectors shall be addressable and intelligent, and shall connect with two wires to the

fire alarm control panel signaling line circuits.

3. Addressable smoke and thermal (heat) detectors shall provide dual alarm and

power/polling LEDs. Both LEDs shall flash under normal conditions, indicating that the

detector is operational and in regular communication with the control panel, and both

LEDs shall be placed into steady illumination by the control panel, indicating that an

alarm condition has been detected. An output connection shall also be provided in the

base to connect an external remote alarm LED.

4. Using software in the FACP, detectors shall automatically compensate for dust

accumulation and other slow environmental changes that may affect their performance.

The detectors shall be listed by UL as meeting the calibrated sensitivity test

requirements of NFPA Standard 72, Chapter 10.

5. Detectors shall be ceiling-mount and shall include a separate twist-lock base with

tamper proof feature. Base options shall include a base with a built-in (local) sounder

rated for a minimum of 85 DBA, a relay base and an isolator base designed for Style 7

applications.

6. Detectors shall provide a test means whereby they will simulate an alarm condition and

report that condition to the control panel.

7. Detectors shall also store an internal identifying type code that the control panel shall

use to identify the type of device (ION, PHOTO, THERMAL).

8. Detectors shall provide address-setting means using decimal switches.

1.11. BATTERIES:

A. Upon loss of Primary (AC) power to the control panel, the batteries shall have sufficient

capacity to power the fire alarm system for required standby time (24 or 60 hours)

followed by 5 minutes of alarm.

B. The batteries are to be completely maintenance free. No liquids are required. Fluid level

checks for refilling, spills, and leakage shall not be required.

C. If necessary to meet standby requirements, external battery/charger systems may be used.

PART 3.0 - EXECUTION

3.1. INSTALLATION:

A. Installation shall be in accordance with the NEC, NFPA 72, local and state codes, as

shown on the drawings, and as recommended by the major equipment manufacturer.

B. All conduit, junction boxes, conduit supports and hangers shall be concealed in finished

areas and may be exposed in unfinished areas. Smoke detectors shall not be installed prior

to the system programming and test period. If construction is ongoing during this period,

measures shall be taken to protect smoke detectors from contamination and physical

damage.

C. All fire detection and alarm system devices, control panels and remote annunciators shall

be flush mounted when located in finished areas and may be surface mounted when

located in unfinished areas.

D. Manual pull stations shall be suitable for surface mounting or semi-flush mounting as

shown on the plans, and shall be installed not less than 42 inches (1067 mm), nor more

than 48 inches (122 mm) above the finished floor.

3.2. TEST:

The service of a competent, NICET level II technician shall be provided to technically

supervise and participate during all of the adjustments and tests for the system. All testing

shall be in accordance with NFPA 72, Chapter 10.

A. Before energizing the cables and wires, check for correct connections and test for short

circuits, ground faults, continuity, and insulation.

B. Close each sprinkler system flow valve and verify proper supervisory alarm at the FACP.

C. Verify activation of all waterflow switches.

D. Open initiating device circuits and verify that the trouble signal actuates.

E. Open and short signaling line circuits and verify that the trouble signal actuates.

F. Open and short notification appliance circuits and verify that trouble signal actuates.

G. Ground all circuits and verify response of trouble signals.

H. Check presence and audibility of tone at all alarm notification devices.

I. Check installation, supervision, and operation of all intelligent smoke detectors using the

walk test.

J. Each of the alarm conditions that the system is required to detect should be introduced on

the system. Verify the proper receipt and the proper processing of the signal at the FACP

and the correct activation of the control points.

K. When the system is equipped with optional features, the manufacturer's manual shall be

consulted to determine the proper testing procedures. This is intended to address such

items as verifying controls performed by individually addressed or grouped devices,

sensitivity monitoring, verification functionality and similar.

3.3. FINAL INSPECTION:

A. At the final inspection, a minimum NICET Level II technician shall demonstrate that the

system functions properly in every respect.

3.4. INSTRUCTION:

A. Instruction shall be provided as required for operating the system. Hands-on

demonstrations of the operation of all system components and the entire system including

program changes and functions shall be provided.

B. The contractor or installing dealer shall provide a user manual indicating "Sequence of

Operation."