# ENGINEERING SPECIFICATION – INTELLIGENT FIRE ALARM SYSTEM

Revision: April 17, 2001

### INTELLIGENT ADDRESSABLE FIRE ALARM DETECTION SYSTEM

## PART 1.0 - GENERAL

### 1.1 DESCRIPTION:

A. 	This section of the specifications includes the furnishing, installation, and connection of the microprocessor controlled, addressable reporting fire alarm equipment required to form a complete coordinated system ready for operation. It shall include, but not be limited to, alarm initiating devices, alarm notification appliances, fire alarm control panel, auxiliary control devices, annunciators, and wiring as shown on the drawings and specified herein.

B. 	The fire alarm system shall comply with requirements of NFPA standard No. 72 for protected premises signaling systems except as modified and supplemented by this specification. The system shall be electrically supervised and monitor the integrity of all conductors.

### 1.2 SCOPE:

A. 	A new addressable reporting, microprocessor controlled fire detection system shall be installed in accordance with the specifications and drawings.

B.	Basic Performance:

1. 	Alarm, trouble and supervisory signals from all intelligent addressable reporting devices shall be encoded onto a Class B (NFPA Style 4), or Class A (NFPA Style 6, 7) Signaling Line Circuit (SLC).

2. 	Initiation Device Circuits (IDCs) shall be wired Class B (NFPA Style B) or Class A (NFPA Style D).

3. 	Notification Appliance Circuits shall be wired Class B (NFPA Style Y) or Class A (NFPA Style Z).

4. 	Built-in Horn Strobe Synchronization w/ selective silence.

5. 	Digitized electronic signals shall employ check digits or multiple polling.

6. 	A single ground or open on the system Signaling Line Circuit (SLC) shall not cause system malfunction, loss of operating power or the ability to report an alarm.

7. 	Alarm signals arriving at the main FACP shall not be lost following a power failure (or outage) until the alarm signal is processed and recorded.

C.	Basic System Functional Operation

When a fire alarm condition is detected and reported by one of the system initiating devices the following functions shall immediately occur:

1.	The System Alarm LED shall flash.

2.	A local piezo electric signal in the control panel shall sound.

3.	A 80-character, backlit LCD display shall indicate all information associated with the Fire Alarm condition, including the type of alarm point and its location within the protected premises.

4.	Printing and history storage equipment shall log the information associated with each new Fire Alarm Control Panel condition, along with time and date of occurrence.

5.	All system output programs assigned via control-by-event equations to be activated by the particular point in alarm shall be executed, and the associated System Outputs (alarm Notification Appliances and/or Relays) shall be activated.

### 1.3 SUBMITTALS

A. 	General:

1. 	Two copies of all submittals shall be submitted to the Architect/Engineer for review.

2. 	All references to manufacturer's model numbers and other pertinent information herein is intended to establish minimum standards of performance, function and quality. Equivalent equipment (compatible UL-Listed) from other manufacturers may be substituted for the specified equipment as long as the minimum standards are met.

3. 	For equipment other than that specified, the contractor shall supply proof that such substitute equipment equals or exceeds the features, functions, performance, and quality of the specified equipment.

B. 	Shop Drawings:

1. 	Sufficient information, clearly presented, shall be included to determine compliance with drawings and specifications.

2. 	Include manufacturer's name(s), model numbers, ratings, power requirements, equipment layout, device arrangement, complete wiring point-to-point diagrams, and conduit layouts.

3. 	Show remote annunciator(s) layout, configurations, and terminations.

C. 	Manuals:

1. 	Submit simultaneously with the shop drawings, complete operating and maintenance manual listing the manufacturer's name(s) including technical data sheets.

2. 	Wiring diagrams shall indicate internal wiring for each item of equipment and the interconnections between the items of equipment.

3. 	Provide a clear and concise description of operation that gives, in detail, the information required to properly operate the equipment and system.

D. 	Certifications:

Together with the shop drawing submittal, submit a certification from the major equipment manufacturer indicating that the proposed supervisor of installation and the proposed performer of contract maintenance is an authorized representative of the major equipment manufacturer. Include names and addresses in the certification.

### 1.4 GUARANTEE:

All work performed and all material and equipment furnished under this contract shall be free from defects and shall remain so for a period of at least one (1) year from the date of acceptance. The full cost of maintenance, labor and materials required to correct any defect during this one-year period shall be included in the submittal bid.

### 1.5 MAINTENANCE:

Maintenance and testing shall be on a semi-annual basis or as required by the local AHJ. A preventive maintenance schedule shall be provided by the Contractor that shall describe the protocol for preventive maintenance. The schedule shall include:

1. 	Systematic examination, adjustment and cleaning of all detectors, manual fire alarm stations, control panels, power supplies, relays, water flow switches and all accessories of the fire alarm system.

2. 	Each circuit in the fire alarm system shall be tested semi-annually.

3. 	Each smoke detector shall be tested in accordance with the requirements of NFPA 72 Chapter 7.

### 1.6 POST CONTRACT EXPANSIONS:

A. 	The contractor shall provide parts and labor to expand the system specified, if so requested, for a period of one (1) year from the date of acceptance.

B. 	As part of the submittal include a quotation for all parts and material, and all installation and test labor as needed to increase the number of addressable devices by ten percent (10%). This quotation shall include addressable smoke detectors, addressable heat detectors, addressable duct detectors, addressable manual stations, addressable monitor modules and addressable control modules equal in number to one tenth of the number required to meet this specification (list actual quantity of each type).

C. 	Quotation shall include installation and test labor and labor to reprogram the system for this 10% expansion. If additional FACP hardware would be required, include the material and labor necessary to install this hardware.

D. 	Submittals that do not include this estimate of post contract expansion cost will not be accepted.

### 1.7 APPLICABLE SPECIFICATIONS:

The specifications and standards listed below form a part of this specification. The system shall fully comply with these standards.

A. 	National Fire Protection Association (NFPA) - USA:

No. 70 National Electrical Code (NEC)

No. 72 Central Station Signaling Systems

No. 72 Protective Signaling Systems

No. 72 Automatic Fire Detectors

No. 72 Notification Appliances for Protective Signaling Systems.

No. 72 Testing Procedures for Signaling Systems.

No. 101 Life Safety Code

B. 	Underwriters Laboratories Inc. (UL) - USA:

No. 268 Smoke Detectors for Fire Protective Signaling Systems

No. 864 Control Units for Fire Protective Signaling Systems

No. 268ASmoke Detectors for Duct Applications.

No. 521 Heat Detectors for Fire Protective Signaling Systems

No. 464 Audible Signaling Appliances.

No. 38 Manually Actuated Signaling Boxes.

No. 346 Waterflow Indicators for Fire Protective Signaling Systems.

No. 1971Visual Notification Appliances for the hearing impaired.

C. 	Local and State Building Codes

D. 	All requirements of the Authority Having Jurisdiction (AHJ).

### 1.8 APPROVALS:

The system shall have proper listing and/or approval from the following nationally recognized agencies:

- UL Underwriters Laboratories Inc.

- FM Factory Mutual Systems

- CSFM California State Fire Marshal

- MEA NYC Materials and Equipment Acceptance

- ULC Underwriters Laboratories of Canada

## PART 2.0 PRODUCTS

### 2.1 EQUIPMENT AND MATERIAL, GENERAL:

A. 	All equipment and components shall be new, and the manufacturer's current model. The materials, appliances, equipment and devices shall be tested and listed by a nationally recognized approvals agency for use as part of a protected premises protective signaling (fire alarm) system.

B. 	All equipment and components shall be installed in strict compliance with manufacturers' recommendations. Consult the manufacturer's installation manuals for all wiring diagrams, schematics, physical equipment sizes, etc., before beginning system installation.

C. 	All Equipment shall be attached to walls and ceiling/floor assemblies and shall be held firmly in place (e.g., detectors shall not be supported solely by suspended ceilings). Fasteners and supports shall be adequate to support the required load.

D. 	Equipment should be manufactured by an ISO 9001 Certified Company.

### 2.2 CONDUIT AND WIRE:

A. 	Conduit:

1.	Conduit shall be in accordance with The National Electrical Code (NEC), local and state       requirements.

2.	Conduit fill shall not exceed 40 percent of interior cross sectional area where three or more cables are contained within a single conduit.

3.	Cable must be separated from any open conductors of Power, or Class 1 circuits, and shall not be placed in any conduit, junction box or raceway containing these conductors, as per NEC Article 760-29.

4.	Wiring for 24 volt control, alarm notification, emergency communication and similar power limited auxiliary functions may be run in the same conduit as initiating and signaling line circuits. All circuits shall be provided with transient suppression devices and the system shall be designed to permit simultaneous operation of all circuits without interference or loss of signals.

5.	Conduit shall not enter the Fire Alarm Control Panel, or any other remotely mounted Control Panel equipment or backboxes, except where conduit entry is specified by the FACP manufacturer.

6.	Conduit shall be 3/4-inch (19.1 mm) minimum.

B. 	Wire:

1. 	Wiring shall be in accordance with local, state and national codes (e.g., NEC Article 760) and as recommended by the manufacturer of the fire alarm system. Number and size of conductors shall be as recommended by the fire alarm system manufacturer, but not less than 18 AWG (1.02 mm) for Initiating Device Circuits and Signaling Line Circuits, and 14 AWG (1.63 mm) for Notification Appliance Circuits.

2.	All wire and cable shall be listed and/or approved by a recognized testing agency for use with a protective signaling system.

3.	Wire and cable not installed in conduit shall have a fire resistance rating suitable for the installation as indicated in NFPA 70 (e.g., FPLR).

4.	Wiring used for the multiplex communication loop shall be twisted and shielded and installed in conduit unless specifically excepted by the fire alarm equipment manufacturer. The system shall permit use of IDC and NAC wiring in the same conduit with the communication loop.

5. 	All field wiring shall be completely supervised.

C. 	Terminal Boxes, Junction Boxes and Cabinets:

D. 	All boxes and cabinets shall be UL listed for their use and purpose.

E. 	The Fire Alarm Control Panel shall be connected to a separate dedicated branch circuit, maximum 20 amperes. This circuit shall be labeled at the Main Power Distribution Panel as FIRE ALARM. Fire Alarm Control Panel Primary Power wiring shall be 12 AWG. The Control Panel Cabinet shall be grounded securely to either a cold water pipe or grounding rod.

### 2.3 MAIN FIRE ALARM CONTROL PANEL:

A. 	The FACP shall be a Fire-Lite Alarms model MS-9600 and shall contain a microprocessor based Central Processing Unit (CPU). The CPU shall communicate with and control the following types of equipment used to make up the system: addressable detectors, addressable modules, printer, annunciators, and other system controlled devices.

B. 	System Capacity and General Operation

1.	The control panel shall provide, or be capable of expansion to 318 addressable detectors and 318 monitor or control modules (636 addressable devices).

2.	The Fire Alarm Control Panel shall include a full featured operator interface control and annunciation panel that shall include a backlit, 80-character Liquid Crystal Display, individual, color coded system status LEDs, and an alphanumeric keypad for the Field Programming and control of the Fire Alarm System.

3.	All programming or editing of the existing program in the system shall be achieved without special equipment and without interrupting the alarm monitoring functions of the Fire Alarm Control Panel.

4.	The FACP shall provide the following features: Maintenance Alert to warn of excessive detector dirt or dust. Detector sensitivity read/test information and System Status Reports to display or print. Smoke Detector Alarm Verification. Pre-signal, meeting NFPA 72 requirements. Rapid manual station reporting (under 3 seconds). Periodic Detector Test, conducted automatically by the control panel every two hours. March time, temporal (ANSI Cadence) and California Code coding options. Walk Test will check for two detectors set to same address.

5.	The main CPU shall contain Form-C relay contacts rated at 2.0 amps/30VDC for the following: Alarm, Trouble, Supervisory.

6.	The CPU shall contain two Class B or A (NFPA Style Y or Z) programmable Notification Appliance Circuits.

C. 	Central Microprocessor

1.	The Microprocessor shall communicate with, monitor, and control all external interfaces with the control panel. It shall include EPROM for system program storage; non-volatile memory for building-specific program storage; and a "watch dog" timer circuit to detect and report microprocessor failure.

2.	The Microprocessor shall contain and execute all programming for specific action to be taken if an alarm condition is detected by the system. Such programming shall be held in non-volatile programmable memory and shall not be lost if both the system primary and secondary power failure occurs.

3.	he Microprocessor Unit shall also provide a Real- Time Clock for time annotation of system displays, printer, and history file.

4. 	The Microprocessor Unit shall contain flash memory capabilities for easy upload/download for upgrades of software.

5. 	All clock, date and history files shall be maintained during power loss.

D. 	Display

1.	The Display shall provide all the controls and indicators used by the system operator and may also be used to program all system operational parameters.

2.	The Display shall include status information and custom alphanumeric labels for all Addressable Detectors, Addressable Modules and Software zones.

3.	The Display shall provide a 80-character backlit alphanumeric Liquid Crystal Display (LCD). It shall also provide 9 Light-Emitting-Diodes (LEDs), consisting of and not limited to the following: AC POWER, FIRE ALARM, SUPERVISORY, SYSTEM TROUBLE, MAINTENANCE, ALARM SILENCED, DISABLED, BATTERY, and GROUND.

4.	The Display shall provide a 25-key touch key-pad with control capability to command all system functions, entry of any alphabetic or numeric information, and field programming. Two different password levels shall be provided to prevent unauthorized system control or programming.

5.	The Display shall include the following operator switches: ACKNOWLEDGE/STEP ALARM SILENCE, DRILL, and SYSTEM RESET (also serving as a lamp test switch).

E. 	Signaling Line Circuit Interface

1.	The SLC Interface shall provide power to, and communicate with, all of the Addressable Detectors and Addressable Modules over a single pair of wires. This SLC Loop shall be capable of NFPA Style 4, Style 6, or Style 7 operation.

2.	The SLC interface shall receive information from all Addressable Devices. This information shall be processed to determine whether normal, alarm, or trouble conditions exist for each detector. This information may also be used for automatic detector testing and for the automatic determination of detector maintenance requirements.

3.	The Signaling Line Circuit shall be capable of distances of 10,000 feet (@ 12 AWG, twisted). For retrofit applications, the system shall support up to 3,000 feet of untwisted, unshielded wire. (Loop 1 only)

F. 	Serial Interfaces

1. 	An EIA-232 interface between the Fire Alarm Control Panel and UL Listed Electronic Data Processing (EDP) peripherals shall be provided. The EIA-232 interface shall allow the use of printers, or for an interface to an off-line PC programmer.

2.	An EIA-485 port shall be available for the serial connection of optional remote led-type annunciators. EIA-485 in terminal mode shall allow serial connection of optional LCD, English language remote system displays. LED (per zone or point) annunciators shall also be provided. The maximum distance to the furthest annunciator shall be 3,000 feet. The system shall support a maximum of 32, remote annunciators on a single twisted, shielded pair. The maximum distance to the furthest annunciator shall be 6,000 feet.

3. 	A PS2/PC keyboard connection shall be provided to support the connection of a PC keyboard for local programming of the fire alarm system.

G. 	Enclosures:

1.	The control panel shall be housed in a UL listed cabinet suitable for surface or semi-flush mounting. Cabinet and front shall be corrosion protected.

2.	The door shall provide a key lock and shall include a glass or other transparent opening for viewing of all indicators.

3. 	An optional semi-flush trim ring shall be available for a neat cabinet dress.

H. 	All interfaces and associated equipment are to be protected so that they will not be affected by voltage surges or line transients consistent with UL standard 864.

I. 	Optional plug-in modules shall be provided for NFPA 72 auxiliary and remote station fire alarm systems as well as a Digital Alarm Communicator Transmitter for NFPA 72 Central Station systems. The DACT (Fire-Lite Alarms model UDACT) shall meet all current UL requirements for delayed AC fail reporting and shall be capable of reporting individual signals for all 636 points.

J. 	Optional modules (FireLite Alarms model ACM-8RF) shall provide eight Form-C relays rated at 5.0 amps (Relays shall track programmable software zones) and (Fire-Lite Alarms model 4XTMF) Municipal box connection and reverse polarity connection.

K. 	Power Supply:

1.	The Power Supply shall operate on 120 VAC, 60 Hz, and shall provide all necessary power for the FACP.

a. 	240 VAC, 50 Hz version shall be available where required.

2.	It shall provide a minimum of 6.0 amps of usable Notification Appliance power.

3.	It shall provide a battery charger for 24 or 60 hours of standby using dual-rate charging techniques for fast battery recharge.

4.	It shall provide a very low frequency sweep earth detect circuit, capable of detecting earth faults on sensitive addressable modules.

5.	It shall be power-limited using fuse-less, quick-acting electronic circuitry meeting the latest UL requirements.

L. 	Operators Controls

1.	Acknowledge Switch:

a. 	Activation of the control panel Acknowledge switch in response to new Alarms and/or Troubles shall silence the local panel piezo electric signal and change the Alarm and Trouble LEDs from flashing mode to steady-ON mode. If multiple Alarm or Trouble conditions exist, depression of this switch shall advance the 80-character LCD display to the next Alarm or Trouble condition.

b. 	Depression of the Acknowledge switch shall also silence all remote annunciator piezo sounders.

2.	Signal Silence Switch: Activation of the Signal Silence Switch shall cause all programmed Notification Appliances and relays to return to the normal condition after an alarm condition. The selection of Notification circuits and relays that are silenceable by this switch shall be fully field programmable within the confines of all applicable standards. The FACP software shall include silence inhibit, auto-silence timers, and an option to silence horns and keep strobes flashing.

3.	System Reset Switch: Activation of the System Reset Switch shall cause all electronicallylatched initiating devices, appliances or software zones, as well as all associated output devices and circuits, to return to their normal condition. Holding the RESET switch shall perform a Lamp Test function.

4.	Drill (Evacuate) Switch: Press and hold of the Drill switch shall activate all Silenceable Notification Appliance circuits. The Drill function shall latch until press of Signal Silence or Reset.

M. 	Printer

A printer may be connected to provide hard-copy printout of all changes in status of the system and shall time-stamp such printouts with the current time-of-day and date. The printer shall communicate with the control panel using an interface complying with Electrical Industries Association standard EIA-232D.

N. 	Field Programming

1.	The system and its respective devices (i.e. smoke detectors and modules) shall be programmable, configurable and expandable in the field without the need for special tools or electronic equipment and shall not require field replacement of electronic integrated circuits.

2.	All programming may be accomplished through the standard FACP built-in keypad. As well through using a PC keyboard (connection provided on UNIMODE-9600 main circuit board.)

3.	All field-defined programs shall be stored in non-volatile memory and shall not be lost if AC mains and/or battery is lost.

4.	The programming function shall be enabled with a password that may be defined specifically for the system when it is installed. Two levels of password protection shall be provided in addition to a key-lock cabinet. One level is used for status level changes such as zone disable or manual on/off commands. A second (higher-level) is used for actual change of program information.

5.	Program edit shall not interfere with normal operation and fire protection. If a fire condition is detected during programming operation, the system shall exit programming and perform fire protection functions as programmed.

6.	A special program check function shall be provided to detect common operator errors.

7.	An Auto-Program (self-learn) function shall be provided to quickly program initial functions within several seconds. During this operation, smoke detectors connected to the Signaling Line Circuit shall be automatically installed without labor intensive operator key commands and the using additional electronic equipment to program each individual detector.

8.	For flexibility, an optional off-line programming function, with batch upload/download, shall also be available.

O. 	Specific System Operations

1. 	Alarm Verification: The Fire alarm control panel shall have the ability to alarm verify addressable smoke detectors.

2.	Point Disable: Any device in the system may be Enabled or Disabled through the system keypad.

3.	Point Read: The system shall be able to display or print the following point status diagnostic functions: a. Device Status, b. Device Type, c. Device Label, d. Device Zone Assignments and e. Program Parameters

4.	System Status Reports: Upon command from an operator of the system, a status report will be generated and printed, listing all system status.

5. 	Device Sensitivity Reports: Upon command from the operator, the detectors sensitivity can be read and results printed

6.	System History Recording and Reporting: The Fire Alarm Control Panel shall contain a History Buffer that will be capable of storing up to 1,000 system alarms, troubles, or operator actions.

7.	Automatic Detector Maintenance Alert: The Fire Alarm Control Panel shall automatically interrogate each Addressable Smoke Detector and shall analyze the detector responses over a period of time. If any addressable Smoke Detector in the system responds with a reading that is below or above normal limits, then the system will enter the Trouble Mode, and the particular detector will be annunciated on the system display, and printed on the optional printer. This feature shall in no way inhibit the receipt of alarm conditions in the system, nor shall it require any special hardware, special tools or computer expertise to perform.

8.	Software Zones: The FACP shall provide 99 software zones. All addressable devices may be field programmed, to be grouped into these zones for control activation and annunciation purposes. Systems that utilize limited programmability, such as general alarm operation, are unacceptable.

### 2.4 SYSTEM COMPONENTS:

A. 	Programmable Electronic Sounders

1.	Electronic sounders shall operate on 24 VDC nominal.

2.	Electronic sounders shall be field programmable without the use of special tools, to provide slow whoop, continuous, or interrupted tones (Temporal Pattern) with an output sound level of at least 90 dBA measured at 10 feet from the device.

3.	Shall be flush or surface mounted as shown on plans.

B. 	Strobe Lights:

1.	Shall operate on 24 VDC nominal.

2.	Shall meet the requirements of the ADA (Americans with Disabilities Act) as well as UL Standard 1971.

C. 	Audible/Visual Combination Devices:

1.	Shall meet the applicable requirements of Section A listed above for audibility.

2.	Shall meet the requirements of Section B listed above for visibility.

D. 	Addressable Manual Pull Box (Fire-Lite Alarms model BG-12LX)

1.	Addressable Manual Stations shall be provided to connect to the Fire Alarm Control Panel Signaling Line Circuit (SLC) Loops. Up to 159 addressable manual stations may be connected to each SLC loop.

2.	The Manual Pull Box shall, on command from the Control Panel, send data to the panel representing the state of the manual switch. Manual Fire Alarm Stations shall use a key operated test-reset lock, and shall be designed so that after actual emergency operation, they cannot be restored to normal use except by the use of a key.

3.	All operated stations shall have a positive, visual indication of operation that cannot be reset without the use of a key.

4.	Manual Stations shall be constructed of LEXAN (or polycarbonate equivalent) with clearly visible operating instructions provided on the cover. The word FIRE shall appear on the front of the stations in raised letters, 1.75 inches or larger.

5.	Stations shall be suitable for surface mounting, or semiflush mounting as shown on the plans, and shall be installed in accordance with ADA and local codes.

6.	The Manual Station shall provide address-setting means using decimal switches. Addressable manual stations that use binary address setting methods, such as a dip switch, are much more difficult to install and are subject to installation error, and are not allowable substitutes.

E. 	Addressable Photoelectric Detectors (Fire-Lite Alarms model SD350)

1.	Smoke detectors shall be addressable and shall connect with two wires to the Fire Alarm Control Panel Signaling Line Circuit. Up to 318 addressable detectors may connect to two seperate SLC loops.

2.	The detectors shall use the photoelectric (light-scattering) principal to measure smoke density.

3.	The detectors shall be low profile ceiling-mount and shall include a twist-lock base.

4.	The detectors shall provide a test means whereby they will simulate an alarm condition and report that condition to the control panel. Such a test may be initiated at the detector itself (by activating a switch) or initiated remotely on command from the control panel.

5.	The detectors shall provide address-setting means on the detector head using decimal switches. Because of the possibility of installation error, systems that use binary jumpers on dipswitches to set the detector address are not acceptable. The detectors shall also store an internal identifying code that the control panel shall use to identify the type of detector.

6.	The detectors shall provide an alarm and power LED. The LED shall flash under normal conditions, indicating that the detector is operational and in regular communication with the control panel. The LED is placed into steady illumination by the control panel indicating that an alarm condition has been detected. An output connection shall also be provided in the base to connect an external remote alarm LED (Fire-Lite Alarms model RA400Z).

F. 	Addressable Photoelectric Detectors with Fixed Thermal Sensor (Fire-Lite Alarms model SD350T)

1.	Smoke detectors shall be addressable and shall connect with two wires to the Fire Alarm Control Panel Signaling Line Circuit. Up to 318 addressable detectors with fixed thermal sensors (135 degree F) connect to two SLC loops.

2.	The detectors shall use the photoelectric (light-scattering) principal to measure smoke density.

3.	The detectors with fixed thermal sensors shall alarm at a fixed temperature of 135 degree F.

4.	The detectors shall be ceiling-mount and shall include a twist-lock base.

5.	The detectors shall provide a test means whereby they will simulate an alarm condition and report that condition to the control panel. Such a test may be initiated at the detector itself (by activating a switch) or initiated remotely on command from the control panel.

6.	The detectors shall provide address-setting means on the detector head using decimal switches. Because of the possibility of installation error, systems that use binary jumpers on dipswitches to set the detector address are not acceptable. Systems that require a special programmer to set the detector address (including temporary connection at the panel) are labor intensive and not acceptable. The detectors shall also store an internal identifying code that the control panel shall use to identify the type of detector.

7.	The detectors shall provide an alarm and power LED. The LED shall flash under normal conditions, indicating that the detector is operational and in regular communication with the control panel. The LED is placed into steady illumination by the control panel indicating that an alarm condition has been detected. An output connection shall also be provided in the base to connect an external remote alarm LED (Fire-Lite Alarms model RA400Z).

G. 	Addressable Ionization Smoke Detectors (Fire-Lite Alarms model CP350)

1.	Smoke Detectors shall be low profile addressable and connect with two wires to the Fire Alarm Control Panel Signaling Line Circuit. Up to 318 addressable detectors may connect to two SLC loops.

2.	The detectors shall use the dual-chamber ionization principal to measure products of combustion.

3.	The detectors shall be low profile ceiling-mount and shall include a twist-lock base.

4.	The detectors shall provide a test means whereby they will simulate an alarm condition and report that condition to the control panel. Such a test may be initiated at the detector itself, by activating a switch, or may be activated remotely on command from the control panel.

5.	The detectors shall provide address-setting means on the detector head using decimal switches. Because of the possibility of installation error, systems that use binary jumpers or dipswitches to set the address are not acceptable. They shall also store an internal identifying code that the control panel shall use to identify the type of detector.

6.	The detectors shall provide an alarm and power LED. The LED shall flash under normal conditions. The LED is placed into steady illumination by the control panel, indicating that an alarm condition has been detected. An output connection shall also be provided in the base to connect a remote alarm LED (Fire-Lite Alarms model RA400Z).

H. 	Addressable Monitor Module (Fire-Lite Alarms model MMF-300)

1.	Addressable Monitor modules shall be provided to connect one supervised IDC (zone) of conventional Alarm Initiating Devices (any N.O. dry contact device) to the Fire Alarm Control Panel Signaling Line Circuit (SLC) Loop.

2.	The monitor module shall mount in a 4-inch square, 2-1/8" deep electrical box.

3.	The IDC (zone) may be wired for Style D (Class A) or Style B (Class B) operation. The Monitor module shall provide address-setting means using decimal switches and shall also store an internal identifying code that the Fire Alarm Control Panel shall use to identify the type of device. Modules that use binary jumpers or dip-switches are subject to installation errors and are not acceptable. An LED shall be provided that shall flash under normal conditions, indicating that the Monitor module is operational and in regular communication with the control panel.

4.	For difficult to reach areas, the Monitor Module shall be available in a miniature package and shall be no larger than 2-3/4"W x 1-1/4"H x 1/2"D (Fire-Lite Alarms model MMF-301). This version does not support Style D operation or include an LED.

I. 	Addressable 2-Wire Smoke Detector Monitor Module (Fire-Lite Alarms model MMF-302)

1. 	Addressable 2-Wire Smoke Detector Monitor Modules shall be provided to connect one supervised IDC (zone) of two-wire conventional smoke detectors to the Fire Alarm Control Panel Signaling Line Circuit (SLC) Loop.

2.	The monitor module shall mount in a 4-inch square, 2-1/8" deep electrical box.

3. 	The monitor module shall provide terminal connections for a resettable external supply voltage to provide power to the IDC (zone) of two-wire smoke detectors.

4.	The IDC (zone) may be wired for Style D (Class A) or Style B (Class B) operation. The monitor module shall provide address-setting means using decimal switches and shall also store an internal identifying code that the Fire Alarm Control Panel shall use to identify the type of device. Modules that use binary jumpers or dip-switches are subject to installation errors and are not acceptable. An LED shall be provided that shall flash under normal conditions, indicating that the Monitor module is operational and in regular communication with the control panel.

J. 	Addressable Dual-Circuit Monitor Module (Fire-Lite Alarms model MDF-300)

1. 	Addressable Dual-Circuit Monitor Modules shall be provided to connect two supervised IDCs (zones) of conventional Alarm Initiating Devices (any N.O. dry contact device) to the Fire Alarm Control Panel Signaling Line Circuit (SLC) Loop.

2.	The-monitor module shall mount in a 4-inch square, 2-1/8" deep electrical box.

3.	The IDCs (zones) may be wired for Style B (Class B) operation only. The Monitor module shall provide address-setting means using decimal switches and shall also store an internal identifying code that the Fire Alarm Control Panel shall use to identify the type of device. Modules that use binary jumpers or dip-switches are subject to installation errors and are not acceptable. An LED shall be provided that shall flash under normal conditions, indicating that the Monitor module is operational and in regular communication with the control panel.

K. 	Addressable Control Module (Fire-Lite Alarms Model CMF-300)

1.	Addressable Control Modules shall be provided to supervise and control the operation of one conventional Notification Appliance Circuit (NAC) of compatible, 24 VDC powered, polarized Audio/Visual appliances or audio speakers.

2.	The Control Module shall mount in a standard 4-inch square, 2-1/8" deep electrical box or to a surface mounted backbox.

3.	The NAC shall wire in a Class B (Style Y) or Class A (Style Z) fashion. Each control module shall support up to 1 Amp of Inductive or 2 Amps of Resistive Audible/Visual signals.

4.	Audio/Visual power shall be provided by a separate supervised power Loop from the main Fire Alarm Control Panel or from a supervised, UL listed Remote Power Supply.

5.	The Control Module shall provide address-setting means using decimal switches and shall also store an internal identifying code that the Control Panel shall use to identify the type of device. Modules that use binary jumpers or dip-switches are subject to installation errors and are not acceptable. An LED shall be provided that shall flash under normal conditions, indicating that the Control Module is operational and is in regular communication with the control panel.

6.	A magnetic test switch shall be provided to test the module without opening or shorting its NAC circuit wiring.

M. Addressable Relay Module (Fire-Lite Alarms model CRF-300)

1. 	Addressable Relay Modules shall be provided to allow a compatible control panel to switch discrete contacts by code command.

2.	The Relay Module shall mount in a standard 4-inch square, 2-1/8" deep electrical box or to a surface mounted backbox.

3. 	The Relay Module shall provide two isolated sets of Form-C contacts for fan shutdown and other auxiliary control functions.

4. 	The Relay Module contact ratings shall support up to 1 Amp/30 VDC of Inductive load or 2 Amps/30VDC (coded) of Resistive load (up to 3 Amps in non-coded applications). The relay coil shall be magnetically latched to reduce wiring connection requirements and to insure that 100% of all auxiliary relays or may be energized at the same time on the same pair of wires.

5.	The Control Module shall provide address-setting means using decimal switches and shall also store an internal identifying code that the Control Panel shall use to identify the type of device. Modules that use binary jumpers or dip-switches are subject to installation errors and are not acceptable. An LED shall be provided that shall flash under normal conditions, indicating that the Control Module is operational and is in regular communication with the control panel.

6.	A magnetic test switch shall be provided to test the module without opening or shorting its NAC circuit wiring.

N.	 Isolator Module (Fire-Lite Alarms model I300).

1.	Isolator Modules shall be provided to automatically isolate wire-to-wire short circuits on an SLC loop. The Isolator Module shall limit the number of modules or detectors that may be rendered inoperative by a short circuit fault on the SLC Loop. At least one isolator module shall be provided for each floor or protected zone of the building.

2.	If a wire-to-wire short occurs, the Isolator Module shall automatically open-circuit (disconnect) the SLC loop. When the short circuit condition is corrected, the Isolator Module shall automatically reconnect the isolated section of the SLC loop.

3.	The Isolator Module shall not require any address setting, and its operations shall be totally automatic. It shall not be necessary to replace or reset an Isolator Module after its normal operation.

4.	The Isolator Module shall mount in a standard 4-inch deep electrical box or in a surface mounted backbox. It shall provide a single LED that shall flash to indicate that the Isolator is operational and shall illuminate steadily to indicate that a short circuit condition has been detected and isolated.

O. 	Waterflow Switches (System Sensor WFD Series)

1.	Flow switches shall be integral, mechanical, non-coded, non-accumulative retard type.

2.	Flow switches shall have an alarm transmission delay time that is conveniently adjustable from 0 to 60 seconds.

3.	Flow switches shall be located a minimum of one (1) foot from a fitting that changes the direction of the flow and a minimum of three (3) feet from a valve.

P. 	Sprinkler and Standpipe Valve Supervisory Switches:

1.	Each sprinkler system water supply control valve riser or zone control valve, and each standpipe system riser control valve shall be equipped with a supervisory switch. Standpipe hose valves, and test and drain valves shall not be equipped with supervisory switches.

2.	Each Post Indicator Valve (PIV) or main gate valve shall be equipped with a supervisory switch.

3.	Mount switch so as not to interfere with the normal operation of the valve and adjust to operate within two revolutions toward the closed position of the valve control, or when the stem has moved no more than one-fifth of the distance from its normal position.

4.	The mechanism shall be contained in a weatherproof aluminum housing, that shall provide a 3/4-inch tapped conduit entrance and incorporate the necessary facilities for attachment to the valves.

5.	Switch housing to be finished in red baked enamel.

6.	The entire installed assembly shall be tamper proof and arranged to cause a switch operation if the housing cover is removed, or if the unit is removed from its mounting.

7.	Valve supervisory switches shall be provided and connected under this section and installed by mechanical contractor.

Q. 	Serial, LED-Type, Remote Annunciation (Fire-Lite Alarms AFM Series)

1.	The annunciator shall communicate with the fire alarm control panel via an EIA 485 (ACS mode) communications loop and shall annunciate all zones in the system. Up to 32 annunciators may be connected to the EIA 485 communications loop.

2.	The annunciator shall need no more than four wires to connect to the FACP.

3.	The annunciator shall provide a red Alarm LED per zone, and a yellow Trouble LED per zone. The annunciator will also have an "ON-LINE" LED, local piezo sounder, local acknowledge/lamp test switch, and custom zone/function identification labels.

4.	The annunciator switches may be used for System control such as, Global Acknowledge, Global Signal Silence, and Global System Reset.

R. 	Serial, LCD-Type, Remote System Display (Fire-Lite Alarms LCD-80 Series)

1.	The annunciator shall communicate with the fire alarm control panel via an EIA-485 (Terminal Mode) communications loop and shall include a 80-character, backlit, LCD display which mimics the integral fire alarm control panel LCD display. Up to 32 annunciators may be connected to the EIA-485 communications loop.

2.	The annunciator shall require no more than four wires on the communication loop (two for communication, two for supervision) and two additional wires for power.

3.	In addition to the LCD, English language display, the annunciator shall also include a Power LED, Alarm LED, Trouble LED and Supervisory LED.

4.	A local piezo sounder shall also be included on the annunciator.

5.	Switches for Acknowledge/Lamp Test, Silence, Drill and Reset shall be included on the annunciator protected from unauthorized usage by a key switch (keyed alike to the host FACP).

### 2.5 BATTERIES:

A.	Shall be 12 volt, Gell-Cell type (two required).

B.	Batteries (two required) shall have sufficient capacity to power the fire alarm system for not less than twenty-four hours plus 5 minutes of alarm upon a normal AC power failure.

C.	The batteries are to be completely maintenance free. No liquids are required. Fluid level checks refilling, spills and leakage shall not be required.

## PART 3.0 - EXECUTION

### 3.1 INSTALLATION:

A. 	Installation shall be in accordance with the NEC, NFPA 72, local and state codes, as shown on the drawings, and as recommended by the major equipment manufacturer.

B. 	All conduit, junction boxes, conduit supports and hangers shall be concealed in finished areas and may be exposed in unfinished areas. Smoke detectors shall not be installed prior to the system programming and test period. If construction is ongoing during this period, measures shall be taken to protect smoke detectors from contamination and physical damage.

C. 	All fire detection and alarm system devices, control panels and remote annunciators shall be flush mounted when located in finished areas and may be surface mounted when located in unfinished areas.

### 3.2 TEST:

Provide the service of a competent, factory-trained engineer or technician authorized by the manufacturer of the fire alarm equipment to technically supervise and participate during all of the adjustments and tests for the system.

1.	Before energizing the cables and wires, check for correct connections and test for short circuits, ground faults, continuity, and insulation.

2.	Close each sprinkler system flow valve and verify proper supervisory alarm at the FACP.

3.	Verify activation of all flow switches.

4.	Open initiating device circuits and verify that the trouble signal actuates.

5.	Open and short signaling line circuits and verify that the trouble signal actuates.

6.	Open and short Notification Appliance Circuits and verify that trouble signal actuates.

7.	Ground all circuits and verify response of trouble signals.

8.	Check presence and audibility of tone at all alarm notification devices.

9.	Check installation, supervision, and operation of all addressable smoke detectors using the Walk Test.

10.	Each of the alarm conditions that the system is required to detect should be introduced on the system. Verify the proper receipt and the proper processing of the signal at the FACP and the correct activation of the control points.

11.	When the system is equipped with optional features, the manufacturer's manual should be consulted to determine the proper testing procedures. This is intended to address such items as verifying the controls performance by individually addressed or grouped devices, sensitivity monitoring, verification functionality and similar.

### 3.3 FINAL INSPECTION:

At the final inspection, a manufacturer-trained representative shall demonstrate that the system functions properly in every respect.

### 3.4 INSTRUCTION:

Provide instruction as required for operating the system. "Hands-on" demonstrations of the operation of all system components and the entire system including program changes and functions shall be provided. The Contractor and/or the Systems Manufacturer's representatives shall provide a typewritten "Sequence of Operation" to the Owner if required.