## 5012 calc
MS-5012 Battery Calculation
**Since the current draws listed here can be edited, the user is fully responsible for verifying these calculations.**
Entries only to be made in the Yellow cell locations
| Regulated Load in Standby |  |  |  | Page 1
| Number of |  | Current |  | Total Current
Device Type | Devices |  | (Amps) |  | (Amps)
Main Circuit Board | 1 | X | 0.074 | = | 0.074
ADM-12 |  | X | 0.012 | = | 0
RZA-5F |  | X | 0.012 | = | 0
2-Wire Detector Heads |  | X |  | = | 0
4-Wire Detector Heads |  | X |  | = | 0
Power Supervision Relays |  | X | 0.025 | = | 0
Auxiliary Outputs
TB3-4 Alarm (1 max.) |  | X | 0 | = | 0
TB3-5 Trouble (1 max.) |  | X | 0.04 | = | 0
TB3-6 Supervisory (1 max.) |  | X | 0 | = | 0
TB3-7 Comm. Fail (1 max.) |  | X | 0 | = | 0
Additional Current Draw from |  | X |  | = | 0
TB-3 (non alarm)
SUM COLUMN FOR STANDBY LOAD |  |  | 0.074 | = | AMPS
MS-5012 Battery Calculation
**Since the current draws listed here can be edited, the user is fully responsible for verifying these calculations.**
Entries only to be made in the Yellow cell locations
| Regulated Load in ALARM |  |  |  | Page 2
| Number of |  | Current |  | Total Current
Device Type | Devices |  | (Amps) |  | (Amps)
MAIN CIRCUIT BOARD | 1 | X | 0.17 | = | 0.17
ADM-12 (1 max.) | 0 | X | 0.032 | = | 0
RZA-5F (1 max.) | 0 | X | 0.03 | = | 0
4-Wire Smoke Detectors | 0 | X |  | = | 0
Power Supervision Relays | 0 | X | 0.025 | = | 0
Auxiliary Outputs
TB3-4 Alarm (1 max.) | 0 | X | 0.04 |  | 0
TB3-5 Trouble (1 max.) | 0 | X | 0.04 | = | 0
TB3-6 Supervisory (1 max.) | 0 | X | 0 |  | 0
TB3-7 Comm. Fail (1 max.) | 0 | X | 0 | = | 0
Notification Appliances |  | X |  | = | 0
ADDITIONAL CURRENT FROM |  | X |  | = | 0
TB-3 (ALARM CURRENT)
SUM COLUMN FOR LOAD IN ALARM |  |  | 0.17 | = | AMPS
MS-5012 Battery Calculation
**Since the current draws listed here can be edited, the user is fully responsible for verifying these calculations.**
Entries only to be made in the Yellow cell locations
| Calculation Total Sheet |  |  |  | Page 3
Use the total standby and alarm load currents calculated in tables A-2A and A-2B for the
following battery calculations
Standby Load |  |  | Required Standby Time in Hours
Current (Amps) |  |  | (24 or 60 Hrs.)
| 0.074 | X | 24 | = | 1.776
Alarm Load |  |  | Required Alarm Time in Hours
Current (Amps) |  |  | (5 minutes = 0.084)
| 0.17 | X | 0.084 | = | 0.01428
Add Standby and Alarm Load for Required
Ampere Hour Battery |  |  |  |  | 1.7903
Multiply by the Derating Factor of 1.2
Total Ampere Hours Required |  |  |  | = | 2.1483
Battery Check
The batteries can be housed in the panel cabinet
The panel is capable of charging the required batteries
Current Draw Check
The total NAC output current is within the limitations of the panel