## Power Supply Config
|  |  | Project Name: |  |  |  | Standby Hours: |  | 24
|  |  | Project ID: |  |  |  | Alarm Mins: |  | 5
|  |  | Prepared By: |  |  |  | Derating Factor: |  | 1.2
5496 Power Expander Calculations |  |  |  | Date: |  |  | Voltage Drop Warning Threshold % :
Version 02.24.09 | [8 empty] | 10
Panel ID: | 5496 |  | Model: | 5496 Power Expander |  |  | Max NAC Current: |  | 3.0 Amps
Location: |  |  | Volts: | 24 VDC |  |  | Max Panel Current: |  | 6.0 Amps
Part.# | Description | Qty | Current Draw |  | Wire AWG | Ohms Per | Length(ft) | Actual | Volts @ | %Drop
|  |  | Standby | Alarm | & Type | 1000 Ft. | One-Way | Ohms | EOL
5496 | 5496 Pwr Module | 1 | 0.04 | 0.16
NAC #1 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
NAC #2 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
NAC #3 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
NAC #4 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
Total Standby Current (Amps) |  |  | 0.04 | 0.16 | Total Alarm Current (Amps)
Standby Time In Hours |  |  | 24 | 0.083333 | Alarm Time In Minutes / 60 |  | (5 Mins)
Total Standby AH Required |  |  | 0.96 | 0.013333 | Total Alarm AH Required
Total Combined AH Required |  |  | 0.97333 |  | Command Shortcuts
Multiply By The Derating Factor |  |  | 1.2
Minimum Battery AmpHours Required |  |  | 1.168

## Smokes
Device Database
Device Database
Command Shortcuts
Item# | Device / Description | Current Draw In Amperes
|  | Standby | Alarm
1 | Unused
2 | Gentex GCC24 Horn/Strobe (15cd) | 0 | 0.143
3 | Gentex GCC24 Horn/Strobe (30cd) | 0 | 0.153
4 | Gentex GCC24 Horn/Strobe (75cd) | 0 | 0.27
5 | Gentex GCC24 Horn/Strobe (95cd) | 0 | 0.341
6 | Gentex GCC24 Horn/Strobe (115cd) | 0 | 0.383
7 | Gentex GCC24 Horn/Strobe (150cd) | 0 | 0.477
8 | Gentex GCS24 Strobe (15cd) | 0 | 0.12
9 | Gentex GCS24 Strobe (30cd) | 0 | 0.13
10 | Gentex GCS24 Strobe (75cd) | 0 | 0.247
11 | Gentex GCS24 Strobe (95cd) | 0 | 0.318
12 | Gentex GCS24 Strobe (115cd) | 0 | 0.36
13 | Gentex GCS24 Strobe (150cd) | 0 | 0.454
14 | Gentex GEC324 Horn/Strobe (15cd) | 0 | 0.134
15 | Gentex GEC324 Horn/Strobe (30cd) | 0 | 0.152
16 | Gentex GEC324 Horn/Strobe (60cd) | 0 | 0.193
17 | Gentex GEC324 Horn/Strobe (75cd) | 0 | 0.236
18 | Gentex GEC324 Horn/Strobe (110cd) | 0 | 0.28
19 | Gentex GES324 Strobe (15cd) | 0 | 0.078
20 | Gentex GES324 Strobe (30cd) | 0 | 0.096
21 | Gentex GES324 Strobe (60cd) | 0 | 0.137
22 | Gentex GES324 Strobe (75cd) | 0 | 0.18
23 | Gentex GES324 Strobe (110cd) | 0 | 0.224
24 | Gentex GEC24 Horn/Strobe (15cd) | 0 | 0.133
25 | Gentex GEC24 Horn/Strobe (30cd) | 0 | 0.151
26 | Gentex GEC24 Horn/Strobe (60cd) | 0 | 0.192
27 | Gentex GEC24 Horn/Strobe (75cd) | 0 | 0.235
28 | Gentex GEC24 Horn/Strobe (110cd) | 0 | 0.279
29 | Gentex GEC24 Horn/Strobe (177cd) | 0 | 0.343
30 | Gentex GEH24 Horn | 0 | 0.056
31 | Gentex GES24 Strobe (15cd) | 0 | 0.078
32 | Gentex GES24 Strobe (30cd) | 0 | 0.096
33 | Gentex GES24 Strobe (60cd) | 0 | 0.137
34 | Gentex GES24 Strobe (75cd) | 0 | 0.18
35 | Gentex GES24 Strobe (110cd) | 0 | 0.224
36 | Gentex GES24 Strobe (177cd) | 0 | 0.288
37 | Gentex GX91 Mini-Horn (Continuous) | 0 | 0.015
38 | Gentex GX93 Mini-Horn (Temporal) | 0 | 0.022
39 | Gentex WGE Strobe (75cd) | 0 | 0.18
40 | Gentex WGEC Horn/Strobe (75cd) | 0 | 0.236
41 | Silent Knight end of line relay EOL-1224RLY | 0.015 | 0.015
42 | System Sensor CH Chime | 0 | 0.054
43 | System Sensor CHS Chime/Stobe (15cd) | 0 | 0.07
44 | System Sensor CHS Chime/Stobe (15/75cd) | 0 | 0.081
45 | System Sensor CHS Chime/Strobe (30cd) | 0 | 0.099
46 | System Sensor CHS Chime/Strobe (75cd) | 0 | 0.165
47 | System Sensor CHS Chime/Strobe (95cd) | 0 | 0.189
48 | System Sensor CHS Chime/Strobe (110cd) | 0 | 0.21
49 | System Sensor CHS Chime/Strobe (115cd) | 0 | 0.217
50 | System Sensor HR/HRK/HW Horn | 0 | 0.069
51 | System Sensor MH Mini-Horn | 0 | 0.029
52 | System Sensor P2/PC2 Horn/Strobe (15cd) | 0 | 0.091
53 | System Sensor P2/PC2 Horn/Strobe (15/75cd) | 0 | 0.1
54 | System Sensor P2/PC2 Horn/Strobe (30cd) | 0 | 0.116
55 | System Sensor P2/PC2 Horn/Strobe (75cd) | 0 | 0.176
56 | System Sensor P2/PC2 Horn/Strobe (95cd) | 0 | 0.201
57 | System Sensor P2/PC2 Horn/Strobe (110cd) | 0 | 0.221
58 | System Sensor P2/PC2 Horn/Strobe (115cd) | 0 | 0.229
59 | System Sensor P2/PC2 Horn/Strobe (135cd) | 0 | 0.255
60 | System Sensor P2/PC2 Horn/Strobe (150cd) | 0 | 0.27
61 | System Sensor P2/PC2 Horn/Strobe (177cd) | 0 | 0.302
62 | System Sensor P2/PC2 Horn/Strobe (185cd) | 0 | 0.309
63 | System Sensor S/SC Strobe (15cd) | 0 | 0.066
64 | System Sensor S/SC Strobe (15/75cd) | 0 | 0.077
65 | System Sensor S/SC Strobe (30cd) | 0 | 0.094
66 | System Sensor S/SC Strobe (75cd) | 0 | 0.158
67 | System Sensor S/SC Strobe (95cd) | 0 | 0.181
68 | System Sensor S/SC Strobe (110cd) | 0 | 0.202
69 | System Sensor S/SC Strobe (115cd) | 0 | 0.21
70 | System Sensor S/SC Strobe (135cd) | 0 | 0.228
71 | System Sensor S/SC Strobe (150cd) | 0 | 0.246
72 | System Sensor S/SC Strobe (177cd) | 0 | 0.281
73 | System Sensor S/SC Strobe (185cd) | 0 | 0.286
74 | Wheelock AH24 Horn | 0 | 0.08
75 | Wheelock AS241575 Horn/Strobe (1575cd) | 0 | 0.201
76 | Wheelock AS24MCW Horn/Strobe (15cd) | 0 | 0.168
77 | Wheelock AS24MCW Horn/Strobe (30cd) | 0 | 0.205
78 | Wheelock AS24MCW Horn/Strobe (75cd) | 0 | 0.28
79 | Wheelock AS24MCW Horn/Strobe (110cd) | 0 | 0.347
80 | Wheelock AS24MCWH Horn/Strobe (135cd) | 0 | 0.435
81 | Wheelock AS24MCWH Horn/Strobe (185cd) | 0 | 0.56
82 | Wheelock AS24MCC Horn/Strobe (15cd) | 0 | 0.175
83 | Wheelock AS24MCC Horn/Strobe (30cd) | 0 | 0.218
84 | Wheelock AS24MCC Horn/Strobe (75cd) | 0 | 0.301
85 | Wheelock AS24MCC Horn/Strobe (95cd) | 0 | 0.365
86 | Wheelock AS24MCCH Horn/Strobe (115cd) | 0 | 0.435
87 | Wheelock AS24MCCH Horn/Strobe (177cd) | 0 | 0.56
88 | Wheelock CH70 Chime | 0 | 0.022
89 | Wheelock CH70241575 Chime/Strobe (1575cd) | 0 | 0.112
90 | Wheelock CH7024MCW Chime/Strobe (15cd) | 0 | 0.082
91 | Wheelock CH7024MCW Chime/Strobe (30cd) | 0 | 0.114
92 | Wheelock CH7024MCW Chime/Strobe (75cd) | 0 | 0.187
93 | Wheelock CH7024MCW Chime/Strobe (110cd) | 0 | 0.242
94 | Wheelock CH7024MCWH Chime/Strobe (135cd) | 0 | 0.322
95 | Wheelock CH7024MCWH Chime/Strobe (185cd) | 0 | 0.442
96 | Wheelock CH90 Chime | 0 | 0.022
97 | Wheelock CH9024MCC Chime/Strobe (15cd) | 0 | 0.087
98 | Wheelock CH9024MCC Chime/Strobe (30cd) | 0 | 0.127
99 | Wheelock CH9024MCC Chime/Strobe (75cd) | 0 | 0.211
100 | Wheelock CH9024MCC Chime/Strobe (95cd) | 0 | 0.271
101 | Wheelock CH9024MCCH Chime/Strobe (115cd) | 0 | 0.322
102 | Wheelock CH9024MCCH Chime/Strobe (177cd) | 0 | 0.442
103 | Wheelock HS24 Horn | 0 | 0.11
104 | Wheelock HS24MCC Horn/Strobe (15cd) | 0 | 0.175
105 | Wheelock HS24MCC Horn/Strobe (30cd) | 0 | 0.215
106 | Wheelock HS24MCC Horn/Strobe (75cd) | 0 | 0.299
107 | Wheelock HS24MCC Horn/Strobe (95cd) | 0 | 0.359
108 | Wheelock HS24MCCH Horn/Strobe (115cd) | 0 | 0.41
109 | Wheelock HS24MCCH Horn/Strobe (177cd) | 0 | 0.53
110 | Wheelock HS4241575W Horn/Strobe (1575cd) | 0 | 0.2
111 | Wheelock HS424MCW Horn/Strobe (15cd) | 0 | 0.17
112 | Wheelock HS424MCW Horn/Strobe (30cd) | 0 | 0.202
113 | Wheelock HS424MCW Horn/Strobe (75cd) | 0 | 0.275
114 | Wheelock HS424MCW Horn/Strobe (110cd) | 0 | 0.33
115 | Wheelock HS424MCWH Horn/Strobe (135cd) | 0 | 0.41
116 | Wheelock HS424MCWH Horn/Strobe (185cd) | 0 | 0.53
117 | Wheelock MT24 Multitone Appliance | 0 | 0.142
118 | Wheelock MT241575 Multitone/Strobe (1575cd) | 0 | 0.232
119 | Wheelock MTWP2475 Multitone/Strobe (180cd) | 0 | 0.28
120 | Wheelock MT24MCW Multitone/Strobe (15cd) | 0 | 0.202
121 | Wheelock MT24MCW Multitone/Strobe (30cd) | 0 | 0.234
122 | Wheelock MT24MCW Multitone/Strobe (75cd) | 0 | 0.307
123 | Wheelock MT24MCW Multitone/Strobe (110cd) | 0 | 0.362
124 | Wheelock NH24 Horn | 0 | 0.044
125 | Wheelock NS241575W Horn/Strobe (1575cd) | 0 | 0.148
126 | Wheelock NS24MCW Horn/Strobe (15cd) | 0 | 0.118
127 | Wheelock NS24MCW Horn/Strobe (30cd) | 0 | 0.151
128 | Wheelock NS24MCW Horn/Strobe (75cd) | 0 | 0.228
129 | Wheelock NS24MCW Horn/Strobe (110cd) | 0 | 0.288
130 | Wheelock NS24MCC Horn/Strobe (15cd) | 0 | 0.126
131 | Wheelock NS24MCC Horn/Strobe (30cd) | 0 | 0.168
132 | Wheelock NS24MCC Horn/Strobe (75cd) | 0 | 0.253
133 | Wheelock NS24MCC Horn/Strobe (95cd) | 0 | 0.319
134 | Wheelock NS24MCCH Horn/Strobe (115cd) | 0 | 0.394
135 | Wheelock NS24MCCH Horn/Strobe (177cd) | 0 | 0.521
136 | Wheelock RSS/RSSP241575W Strobe (1575cd) | 0 | 0.09
137 | Wheelock RSS/RSSP24MCW Strobe (15cd) | 0 | 0.06
138 | Wheelock RSS/RSSP24MCW Strobe (30cd) | 0 | 0.092
139 | Wheelock RSS/RSSP24MCW Strobe (75cd) | 0 | 0.165
140 | Wheelock RSS/RSSP24MCW Strobe (110cd) | 0 | 0.22
141 | Wheelock RSS/RSSP24MCWH Strobe (135cd) | 0 | 0.3
142 | Wheelock RSS/RSSP24MCWH Strobe (185cd) | 0 | 0.42
143 | Wheelock RSS/RSSP24MCC Strobe (15cd) | 0 | 0.065
144 | Wheelock RSS/RSSP24MCC Strobe (30cd) | 0 | 0.105
145 | Wheelock RSS/RSSP24MCC Strobe (75cd) | 0 | 0.189
146 | Wheelock RSS/RSSP24MCC Strobe (95cd) | 0 | 0.249
147 | Wheelock RSS/RSSP24MCCH Strobe (115cd) | 0 | 0.3
148 | Wheelock RSS/RSSP24MCCH Strobe (177cd) | 0 | 0.42
149 | User Defined
150 | User Defined
151 | User Defined
152 | User Defined
153 | User Defined
154 | User Defined
155 | User Defined
156 | User Defined
157 | User Defined
All of the devices shown in this table will appear as choices in the dropdown boxes used to configure each circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.

## Circuit Config
Circuit Configuration
Project Name: | 0 | Project ID: |  | 0 | Alarm Mins:
Prepared By: | 0 | Date: |  | 0 | Voltage Drop Warning Threshold % :
Ckt. Number: | NAC #1 | Panel ID: | 5496
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | NAC #2 | Panel ID: | 5496
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | NAC #3 | Panel ID: | 5496
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | NAC #4 | Panel ID: | 5496
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0

## Devices (hidden)
Device Database
Notification Appliance Database
Item# | Device / Description | Current Draw In Amperes
|  | Standby | Alarm
1 | Unused
2 | Gentex GMH-24-X Horn | 0 | 0.038
3 | Gentex GX90-4 Horn | 0 | 0.015
4 | Gentex GX90S-4-15 Horn | 0 | 0.093
5 | Gentex GX90S-4-1575 Horn | 0 | 0.108
6 | Gentex GXS-4-1575 Strobe | 0 | 0.145
7 | Gentex HG124 Horn | 0 | 0.03
8 | Gentex HS24-110 Horn/Strobe | 0 | 0.14
9 | Gentex HS24-15 Horn/Strobe | 0 | 0.077
10 | Gentex HS24-15/75 Horn/Strobe | 0 | 0.087
11 | Gentex HS24-30 Horn/Strobe | 0 | 0.087
12 | Gentex HS24-60 Horn/Strobe | 0 | 0.114
13 | Gentex HS24-75 Horn/Strobe | 0 | 0.116
14 | Gentex SHG24-110 Horn/Strobe | 0 | 0.25
15 | Gentex SHG24-15/75-C Horn/Strobe | 0 | 0.123
16 | Gentex SHG24-15/75-W Horn/Strobe | 0 | 0.123
17 | Gentex SHG24-15/75-Z Horn/Strobe | 0 | 0.123
18 | Gentex SHG24-30 Horn/Strobe | 0 | 0.123
19 | Gentex SHG24-30/75 Horn/Strobe | 0 | 0.172
20 | Gentex SHG24-60 Horn/Strobe | 0 | 0.145
21 | Gentex ST24-110 Strobe | 0 | 0.11
22 | Gentex ST24-15 Strobe | 0 | 0.047
23 | Gentex ST24-15/75 Strobe | 0 | 0.057
24 | Gentex ST24-30 Strobe | 0 | 0.057
25 | Gentex ST24-60 Strobe | 0 | 0.084
26 | Gentex ST24-75 Strobe | 0 | 0.086
27 | Silent Knight end of line relay EOL-1224RLY | 0.015 | 0.015
28 | System Sensor H12/24 Horn | 0 | 0.025
29 | System Sensor P24110 Horn/Strobe | 0 | 0.165
30 | System Sensor P241575 Horn/Strobe | 0 | 0.074
31 | System Sensor P2430 Horn/Strobe | 0 | 0.092
32 | System Sensor P2475 Horn/Strobe | 0 | 0.148
33 | System Sensor S2415 Strobe | 0 | 0.043
34 | System Sensor S241575 Strobe | 0 | 0.049
35 | System Sensor S2430 Strobe | 0 | 0.067
36 | System Sensor S2475 Strobe | 0 | 0.123
37 | System Sensor SS24110 Strobe | 0 | 0.14
38 | Wheelock AMT-24-IS-VFR Strobe Horn | 0 | 0.04
39 | Wheelock AMT-24-LSM-VFR Strobe Horn | 0 | 0.125
40 | Wheelock AS-24110-HFR Strobe Horn | 0 | 0.202
41 | Wheelock AS-241575-VFR Strobe Horn | 0 | 0.102
42 | Wheelock AS-2415-VFR Strobe Horn | 0 | 0.087
43 | Wheelock AS-2430-VFR Strobe Horn | 0 | 0.135
44 | Wheelock AS-2475-VFR Strobe Horn | 0 | 0.156
45 | Wheelock MIZ-24-R Mini-Horn | 0 | 0.012
46 | Wheelock MIZ-24-W Mini-Horn | 0 | 0.012
47 | User Defined
48 | User Defined
49 | User Defined
50 | User Defined
51 | User Defined
52 | User Defined
53 | User Defined
54 | User Defined
55 | User Defined
56 | User Defined
57 | User Defined
58 | User Defined
59 | User Defined
60 | User Defined
61 | User Defined
62 | User Defined
63 | User Defined
64 | User Defined
65 | User Defined
66 | User Defined
67 | User Defined
68 | User Defined
69 | User Defined
70 | User Defined
71 | User Defined
72 | User Defined
73 | User Defined
74 | User Defined
75 | User Defined
76 | User Defined
77 | User Defined
78 | User Defined
79 | User Defined
80 | User Defined
81 | User Defined
82 | User Defined
83 | User Defined
84 | User Defined
85 | User Defined
86 | User Defined
87 | User Defined
88 | User Defined
89 | User Defined
90 | User Defined
91 | User Defined
92 | User Defined
93 | User Defined
94 | User Defined
95 | User Defined
96 | User Defined
97 | User Defined
98 | User Defined
99 | User Defined
100 | User Defined
101 | User Defined
102 | User Defined
103 | User Defined
104 | User Defined
105 | User Defined
106 | User Defined
107 | User Defined
108 | User Defined
109 | User Defined
110 | User Defined
111 | User Defined
112 | User Defined
113 | User Defined
114 | User Defined
115 | User Defined
116 | User Defined
117 | User Defined
118 | User Defined
119 | User Defined
120 | User Defined
121 | User Defined
122 | User Defined
123 | User Defined
124 | User Defined
125 | User Defined
126 | User Defined
127 | User Defined
128 | User Defined
129 | User Defined
130 | User Defined
131 | User Defined
132 | User Defined
133 | User Defined
134 | User Defined
135 | User Defined
136 | User Defined
137 | User Defined
138 | User Defined
139 | User Defined
140 | User Defined
141 | User Defined
142 | User Defined
143 | User Defined
144 | User Defined
145 | User Defined
146 | User Defined
147 | User Defined
148 | User Defined
149 | User Defined
150 | User Defined
All of the devices shown in this table will appear as choices in the dropdown boxes used to configure each NAC circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.
Command Shortcuts

## Data (hidden)
Conductor Properties NEC Chap. 9
Item | Wire Type | Ohms Per 1000 ft.
1 | #12 Solid | 1.59
2 | #12 Stranded | 1.59
3 | #14 Solid | 2.52
4 | #14 Stranded | 2.52
5 | #16 Solid | 4.02
6 | #16 Stranded | 4.02
7 | #18 Solid | 6.39
8 | #18 Stranded | 6.39
Cell Links For The Wire Type Drop Down Boxes Associated With Each 5395
| 5395(1) | 5395(2) | 5395(3) | 5395(4) | 5395(5) | 5395(6) | 5395(7) | 5395(8)
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
1 | Notification Appl Circuit
2 | Aux Power Circuit
| NAC 1 | 1
| NAC 2 | 1
| NAC 3 | 1
| NAC 4 | 1
| I/O5 | 1
| I/O6 | 1