## Power Supply Config
|  |  | Project Name: |  |  |  | Standby Hours: |  | 24
|  |  | Project ID: |  |  |  | Alarm Mins: |  | 5
|  |  | Prepared By: |  |  |  | Derating Factor: |  | 1.2
5820XL-EVS Calculations |  |  |  | Date: |  |  | Voltage Drop Warning Threshold % :
Version 1.7.13 | [8 empty] | 15
Panel ID: | 5820XL/ECS |  | Model: | 5820XL/EVS Add. Fire Alarm Control |  |  | Max NAC Current: |  | 3.0 Amps
Location: |  |  | Volts: | 24 VDC |  |  | Max Panel Current: |  | 6.0 Amps
Ckt.# | Circuit Name | Qty | Current Draw |  | Wire AWG | Ohms Per | Length(ft) | Actual | Volts @ | %Drop
|  |  | Standby | Alarm | & Type | 1000 Ft. | One-Way | Ohms | EOL
5820XL | 5820XL Control Panel | 1 | 0.275 | 0.44 | N/A
SK | Photo, Photo-T, PhotoR |  | 0 | 0
SK | Ion |  | 0 | 0
SK | Heat, Heat-HT, ROR |  | 0 | 0
SK | Beam, Beam-T |  | 0 | 0
SK | Duct |  | 0 | 0
SK | Acclimate |  | 0 | 0
SK | FIRE-CO |  | 0 | 0
SK | Control |  | 0 | 0
SK | Control-6 |  | 0 | 0
SK | Monitor, Minimon |  | 0 | 0
SK | Monitor-2 |  | 0 | 0
SK | Monitor-10 |  | 0 | 0
SK | Pull-SA, Pull-DA |  | 0 | 0
SK | Relay |  | 0 | 0
SK | Relay-6 |  | 0 | 0
SK | RelayMon-2 |  | 0 | 0
SK | Zone |  | 0 | 0
SK | Zone-6 |  | 0 | 0
SK | Isolator Module |  | 0 | 0
B224BI | Isolator Base |  | 0 | 0
B200SR | Sounder Base |  | 0 | 0
B200S | Sounder Base |  | 0 | 0
B224RB | Relay Base |  | 0 | 0
RTS151 | Magnetic Remote Test |  | 0 | 0
RTS151KEY | Key Activated Test |  | 0 | 0
RA100Z | Remote LED |  | 0 | 0
5815XL | SLC Loop Expander |  | 0 | 0
5860 | LCD Remote Annunc |  | 0 | 0
5824 | Serial/Parallel Module |  | 0 | 0
5496 | Power Expander |  | 0 | 0
5895XL | Power Expander |  | 0 | 0
5865-4 | LED Annunciator (4G) |  | 0 | 0
5865-3 | LED Annunciator (3G) |  | 0 | 0
5880 | LED Driver Module |  | 0 | 0
5883 | Relay Module |  | 0 | 0
EVS-SW24 | Switch Expander |  | 0 | 0
EVS-VCM | Voice Command Module |  | 0 | 0
EVS-50W | 50 Watt Amplifier |  | 0 | 0
EVS-125W | 125 Watt Amplifier |  | 0 | 0
EVS-RVM | Remote Voice Module |  | 0 | 0
PGM-I/O #1 | Notification Appl Circuit | 0 | 0 | 0 | #14 Stranded | 2.52 |  | 0 | 20.4 | 0%
PGM-I/O #2 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
PGM-I/O #3 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
PGM-I/O #4 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
PGM-I/O #5 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
PGM-I/O #6 | Notification Appl Circuit | 0 | 0 | 0 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
Total Standby Current (Amps) |  |  | 0.275 | 0.44 | Total Alarm Current (Amps)
Standby Time In Hours |  |  | 24 | 0.083333 | Alarm Time In Minutes / 60 |  | (5 Mins)
Total Standby AH Required |  |  | 6.6 | 0.036667 | Total Alarm AH Required
Total Combined AH Required |  |  | 6.6367 |  | Command Shortcuts
Multiply By The Derating Factor |  |  | 1.2
Minimum Battery AmpHours Required |  |  | 7.964
Note: The EVS-RCU remote microphone uses the EVS-RVM and the 5860 annunciator. Add one each the EVS-RVM and 5860
quantities for every EVS-RCU used on the system.
Note on F25: The SK-Beam-T draws a maximum of 500 mA from auxiliary power only when the test feature is used. This should be considered when determining auxiliary power capacity but not calculated into current requirements for day to day operation.
Note on G25: The SK-Beam-T draws a maximum of 500 mA from auxiliary power only when the test feature is used. This should be considered when determining auxiliary power capacity but not calculated into current requirements for day to day operation.
Note on F38: Auxiliary power standby draw is 12 mA per SK-Zone module. You will need to add this draw to the auxiliary power you are using.
Note on G38: Auxiliary power alarm draw is 90 mA per SK-Zone module. You will need to add this draw to the auxiliary power you are using.
Note on F39: Auxiliary power standby draw is 50 mA per SK-Zone-6 module. You will need to add this draw to the auxiliary power you are using.
Note on G39: Auxiliary power alarm draw is 270 mA per SK-Zone-6 module. You will need to add this draw to the auxiliary power you are using.
Note on F29: Auxiliary power standby draw is 1.7 mA per SK-Control module. You will need to add this draw to the auxiliary power you are using.
Note on G29: Auxiliary power alarm draw is 7 mA per SK-Control module. You will need to add this draw to the auxiliary power you are using.
Note on F30: Auxiliary power standby draw is 8 mA per SK-Control-6 module. You will need to add this draw to the auxiliary power you are using.
Note on G30: Auxiliary power alarm draw is 20 mA per SK-Control-6 module. You will need to add this draw to the auxiliary power you are using.
Note on F42: Auxiliary power standby draw is .5 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on G42: Auxiliary power alarm draw is 35 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on F26: The SK-DUCT housing contains a vacant mount for a SK-RELAY (sold separately). Current draw for the SK-RELAY is calculated by increasing the SK-RELAY row of the calculation sheet.
Note on G26: The SK-DUCT housing contains a vacant mount for a SK-RELAY (sold separately). Current draw for the SK-RELAY is calculated by increasing the SK-RELAY row of the calculation sheet.
Note on F43: Auxiliary power standby draw is .5 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on G43: Auxiliary power alarm draw is 35 mA per sounder base. You will need to add this draw to the auxiliary power you are using.

## Smokes
Device Database
Device Database
Command Shortcuts
Item# | Device / Description | Current Draw In Amperes
|  | Standby | *Alarm
1 | Unused
2 | Gentex GCC24 Horn/Strobe (15cd) | 0 | 0.143
3 | Gentex GCC24 Horn/Strobe (30cd) | 0 | 0.153
4 | Gentex GCC24 Horn/Strobe (75cd) | 0 | 0.27
5 | Gentex GCC24 Horn/Strobe (95cd) | 0 | 0.341
6 | Gentex GCC24 Horn/Strobe (115cd) | 0 | 0.383
7 | Gentex GCC24 Horn/Strobe (150cd) | 0 | 0.477
8 | Gentex GCS24 Strobe (15cd) | 0 | 0.12
9 | Gentex GCS24 Strobe (30cd) | 0 | 0.13
10 | Gentex GCS24 Strobe (75cd) | 0 | 0.247
11 | Gentex GCS24 Strobe (95cd) | 0 | 0.318
12 | Gentex GCS24 Strobe (115cd) | 0 | 0.36
13 | Gentex GCS24 Strobe (150cd) | 0 | 0.454
14 | Gentex GEC324 Horn/Strobe (15cd) | 0 | 0.134
15 | Gentex GEC324 Horn/Strobe (30cd) | 0 | 0.152
16 | Gentex GEC324 Horn/Strobe (60cd) | 0 | 0.193
17 | Gentex GEC324 Horn/Strobe (75cd) | 0 | 0.236
18 | Gentex GEC324 Horn/Strobe (110cd) | 0 | 0.28
19 | Gentex GES324 Strobe (15cd) | 0 | 0.078
20 | Gentex GES324 Strobe (30cd) | 0 | 0.096
21 | Gentex GES324 Strobe (60cd) | 0 | 0.137
22 | Gentex GES324 Strobe (75cd) | 0 | 0.18
23 | Gentex GES324 Strobe (110cd) | 0 | 0.224
24 | Gentex GEC24 Horn/Strobe (15cd) | 0 | 0.133
25 | Gentex GEC24 Horn/Strobe (30cd) | 0 | 0.151
26 | Gentex GEC24 Horn/Strobe (60cd) | 0 | 0.192
27 | Gentex GEC24 Horn/Strobe (75cd) | 0 | 0.235
28 | Gentex GEC24 Horn/Strobe (110cd) | 0 | 0.279
29 | Gentex GEC24 Horn/Strobe (177cd) | 0 | 0.343
30 | Gentex GEH24 Horn | 0 | 0.056
31 | Gentex GES24 Strobe (15cd) | 0 | 0.078
32 | Gentex GES24 Strobe (30cd) | 0 | 0.096
33 | Gentex GES24 Strobe (60cd) | 0 | 0.137
34 | Gentex GES24 Strobe (75cd) | 0 | 0.18
35 | Gentex GES24 Strobe (110cd) | 0 | 0.224
36 | Gentex GES24 Strobe (177cd) | 0 | 0.288
37 | Gentex GX91 Mini-Horn (Continuous) | 0 | 0.015
38 | Gentex GX93 Mini-Horn (Temporal) | 0 | 0.022
39 | Gentex WGE Strobe (75cd) | 0 | 0.18
40 | Gentex WGEC Horn/Strobe (75cd) | 0 | 0.236
41 | Silent Knight end of line relay EOL-1224RLY | 0.015 | 0.015
42 | System Sensor CH Chime | 0 | 0.054
43 | System Sensor CHS Chime/Stobe (15cd) | 0 | 0.07
44 | System Sensor CHS Chime/Stobe (15/75cd) | 0 | 0.081
45 | System Sensor CHS Chime/Strobe (30cd) | 0 | 0.099
46 | System Sensor CHS Chime/Strobe (75cd) | 0 | 0.165
47 | System Sensor CHS Chime/Strobe (95cd) | 0 | 0.189
48 | System Sensor CHS Chime/Strobe (110cd) | 0 | 0.21
49 | System Sensor CHS Chime/Strobe (115cd) | 0 | 0.217
50 | System Sensor HR/HRK/HW Horn | 0 | 0.069
51 | System Sensor MH Mini-Horn | 0 | 0.029
52 | System Sensor P2/PC2 Horn/Strobe (15cd) | 0 | 0.091
53 | System Sensor P2/PC2 Horn/Strobe (15/75cd) | 0 | 0.1
54 | System Sensor P2/PC2 Horn/Strobe (30cd) | 0 | 0.116
55 | System Sensor P2/PC2 Horn/Strobe (75cd) | 0 | 0.176
56 | System Sensor P2/PC2 Horn/Strobe (95cd) | 0 | 0.201
57 | System Sensor P2/PC2 Horn/Strobe (110cd) | 0 | 0.221
58 | System Sensor P2/PC2 Horn/Strobe (115cd) | 0 | 0.229
59 | System Sensor P2/PC2 Horn/Strobe (135cd) | 0 | 0.255
60 | System Sensor P2/PC2 Horn/Strobe (150cd) | 0 | 0.27
61 | System Sensor P2/PC2 Horn/Strobe (177cd) | 0 | 0.302
62 | System Sensor P2/PC2 Horn/Strobe (185cd) | 0 | 0.309
63 | System Sensor S/SC Strobe (15cd) | 0 | 0.066
64 | System Sensor S/SC Strobe (15/75cd) | 0 | 0.077
65 | System Sensor S/SC Strobe (30cd) | 0 | 0.094
66 | System Sensor S/SC Strobe (75cd) | 0 | 0.158
67 | System Sensor S/SC Strobe (95cd) | 0 | 0.181
68 | System Sensor S/SC Strobe (110cd) | 0 | 0.202
69 | System Sensor S/SC Strobe (115cd) | 0 | 0.21
70 | System Sensor S/SC Strobe (135cd) | 0 | 0.228
71 | System Sensor S/SC Strobe (150cd) | 0 | 0.246
72 | System Sensor S/SC Strobe (177cd) | 0 | 0.281
73 | System Sensor S/SC Strobe (185cd) | 0 | 0.286
74 | Wheelock AH24 Horn | 0 | 0.08
75 | Wheelock AS241575 Horn/Strobe (1575cd) | 0 | 0.201
76 | Wheelock AS24MCW Horn/Strobe (15cd) | 0 | 0.168
77 | Wheelock AS24MCW Horn/Strobe (30cd) | 0 | 0.205
78 | Wheelock AS24MCW Horn/Strobe (75cd) | 0 | 0.28
79 | Wheelock AS24MCW Horn/Strobe (110cd) | 0 | 0.347
80 | Wheelock AS24MCWH Horn/Strobe (135cd) | 0 | 0.435
81 | Wheelock AS24MCWH Horn/Strobe (185cd) | 0 | 0.56
82 | Wheelock AS24MCC Horn/Strobe (15cd) | 0 | 0.175
83 | Wheelock AS24MCC Horn/Strobe (30cd) | 0 | 0.218
84 | Wheelock AS24MCC Horn/Strobe (75cd) | 0 | 0.301
85 | Wheelock AS24MCC Horn/Strobe (95cd) | 0 | 0.365
86 | Wheelock AS24MCCH Horn/Strobe (115cd) | 0 | 0.435
87 | Wheelock AS24MCCH Horn/Strobe (177cd) | 0 | 0.56
88 | Wheelock CH70 Chime | 0 | 0.022
89 | Wheelock CH70241575 Chime/Strobe (1575cd) | 0 | 0.112
90 | Wheelock CH7024MCW Chime/Strobe (15cd) | 0 | 0.082
91 | Wheelock CH7024MCW Chime/Strobe (30cd) | 0 | 0.114
92 | Wheelock CH7024MCW Chime/Strobe (75cd) | 0 | 0.187
93 | Wheelock CH7024MCW Chime/Strobe (110cd) | 0 | 0.242
94 | Wheelock CH7024MCWH Chime/Strobe (135cd) | 0 | 0.322
95 | Wheelock CH7024MCWH Chime/Strobe (185cd) | 0 | 0.442
96 | Wheelock CH90 Chime | 0 | 0.022
97 | Wheelock CH9024MCC Chime/Strobe (15cd) | 0 | 0.087
98 | Wheelock CH9024MCC Chime/Strobe (30cd) | 0 | 0.127
99 | Wheelock CH9024MCC Chime/Strobe (75cd) | 0 | 0.211
100 | Wheelock CH9024MCC Chime/Strobe (95cd) | 0 | 0.271
101 | Wheelock CH9024MCCH Chime/Strobe (115cd) | 0 | 0.322
102 | Wheelock CH9024MCCH Chime/Strobe (177cd) | 0 | 0.442
103 | Wheelock HS24 Horn | 0 | 0.11
104 | Wheelock HS24MCC Horn/Strobe (15cd) | 0 | 0.175
105 | Wheelock HS24MCC Horn/Strobe (30cd) | 0 | 0.215
106 | Wheelock HS24MCC Horn/Strobe (75cd) | 0 | 0.299
107 | Wheelock HS24MCC Horn/Strobe (95cd) | 0 | 0.359
108 | Wheelock HS24MCCH Horn/Strobe (115cd) | 0 | 0.41
109 | Wheelock HS24MCCH Horn/Strobe (177cd) | 0 | 0.53
110 | Wheelock HS4241575W Horn/Strobe (1575cd) | 0 | 0.2
111 | Wheelock HS424MCW Horn/Strobe (15cd) | 0 | 0.17
112 | Wheelock HS424MCW Horn/Strobe (30cd) | 0 | 0.202
113 | Wheelock HS424MCW Horn/Strobe (75cd) | 0 | 0.275
114 | Wheelock HS424MCW Horn/Strobe (110cd) | 0 | 0.33
115 | Wheelock HS424MCWH Horn/Strobe (135cd) | 0 | 0.41
116 | Wheelock HS424MCWH Horn/Strobe (185cd) | 0 | 0.53
117 | Wheelock MT24 Multitone Appliance | 0 | 0.142
118 | Wheelock MT241575 Multitone/Strobe (1575cd) | 0 | 0.232
119 | Wheelock MTWP2475 Multitone/Strobe (180cd) | 0 | 0.28
120 | Wheelock MT24MCW Multitone/Strobe (15cd) | 0 | 0.202
121 | Wheelock MT24MCW Multitone/Strobe (30cd) | 0 | 0.234
122 | Wheelock MT24MCW Multitone/Strobe (75cd) | 0 | 0.307
123 | Wheelock MT24MCW Multitone/Strobe (110cd) | 0 | 0.362
124 | Wheelock NH24 Horn | 0 | 0.044
125 | Wheelock NS241575W Horn/Strobe (1575cd) | 0 | 0.148
126 | Wheelock NS24MCW Horn/Strobe (15cd) | 0 | 0.118
127 | Wheelock NS24MCW Horn/Strobe (30cd) | 0 | 0.151
128 | Wheelock NS24MCW Horn/Strobe (75cd) | 0 | 0.228
129 | Wheelock NS24MCW Horn/Strobe (110cd) | 0 | 0.288
130 | Wheelock NS24MCC Horn/Strobe (15cd) | 0 | 0.126
131 | Wheelock NS24MCC Horn/Strobe (30cd) | 0 | 0.168
132 | Wheelock NS24MCC Horn/Strobe (75cd) | 0 | 0.253
133 | Wheelock NS24MCC Horn/Strobe (95cd) | 0 | 0.319
134 | Wheelock NS24MCCH Horn/Strobe (115cd) | 0 | 0.394
135 | Wheelock NS24MCCH Horn/Strobe (177cd) | 0 | 0.521
136 | Wheelock RSS/RSSP241575W Strobe (1575cd) | 0 | 0.09
137 | Wheelock RSS/RSSP24MCW Strobe (15cd) | 0 | 0.06
138 | Wheelock RSS/RSSP24MCW Strobe (30cd) | 0 | 0.092
139 | Wheelock RSS/RSSP24MCW Strobe (75cd) | 0 | 0.165
140 | Wheelock RSS/RSSP24MCW Strobe (110cd) | 0 | 0.22
141 | Wheelock RSS/RSSP24MCWH Strobe (135cd) | 0 | 0.3
142 | Wheelock RSS/RSSP24MCWH Strobe (185cd) | 0 | 0.42
143 | Wheelock RSS/RSSP24MCC Strobe (15cd) | 0 | 0.065
144 | Wheelock RSS/RSSP24MCC Strobe (30cd) | 0 | 0.105
145 | Wheelock RSS/RSSP24MCC Strobe (75cd) | 0 | 0.189
146 | Wheelock RSS/RSSP24MCC Strobe (95cd) | 0 | 0.249
147 | Wheelock RSS/RSSP24MCCH Strobe (115cd) | 0 | 0.3
148 | Wheelock RSS/RSSP24MCCH Strobe (177cd) | 0 | 0.42
149 | Silent Knight SD500-ANM Notification Module | 0.008 | 0.06
150 | Silent Knight SD500-LED LED Module | 0.01 | 0.22
151 | Silent Knight SD500-SDM Smoke Det Module | 0.02 | 0.106
152 | Silent Knight SD505-6SB Sounder Base | 0.001 | 0.032
153 | Silent Knight SD505-DUCTR Duct w/Relay | 0.02 | 0.062
154 | User Defined
155 | User Defined
156 | User Defined
157 | User Defined
158 | User Defined
159 | User Defined
160 | User Defined
161 | User Defined
162 | User Defined
*Alarm draws are listed as worse case. Consult manufacturer's specification sheet for actual alarm draw with the candela and/or horn mode you are using.
All of the devices shown in this table will appear as choices in the dropdown boxes used to configure each circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.

## Circuit Config
Circuit Configuration
Project Name: | 0 | Project ID: |  | 0 | Alarm Mins:
Prepared By: | 0 | Date: |  |  | Voltage Drop Warning Threshold % :
Ckt. Number: | PGM-I/O #1 | Panel ID: | 5820XL/ECS
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | PGM-I/O #2 | Panel ID: | 5820XL/ECS
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | PGM-I/O #3 | Panel ID: | 5820XL/ECS
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | PGM-I/O #4 | Panel ID: | 5820XL/ECS
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | PGM-I/O #5 | Panel ID: | 5820XL/ECS
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0
Ckt. Number: | PGM-I/O #6 | Panel ID: | 5820XL/ECS
Ckt. Name: | Notification Appl Circuit | I/O Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0

## Devices (hidden)
Device Database
Notification Appliance Database
Item# | Device / Description | Current Draw In Amperes
|  | Standby | Alarm
1 | Unused
2 | Gentex GMH-24-X Horn | 0 | 0.038
3 | Gentex GX90-4 Horn | 0 | 0.015
4 | Gentex GX90S-4-15 Horn | 0 | 0.093
5 | Gentex GX90S-4-1575 Horn | 0 | 0.108
6 | Gentex GXS-4-1575 Strobe | 0 | 0.145
7 | Gentex HG124 Horn | 0 | 0.03
8 | Gentex HS24-110 Horn/Strobe | 0 | 0.14
9 | Gentex HS24-15 Horn/Strobe | 0 | 0.077
10 | Gentex HS24-15/75 Horn/Strobe | 0 | 0.087
11 | Gentex HS24-30 Horn/Strobe | 0 | 0.087
12 | Gentex HS24-60 Horn/Strobe | 0 | 0.114
13 | Gentex HS24-75 Horn/Strobe | 0 | 0.116
14 | Gentex SHG24-110 Horn/Strobe | 0 | 0.25
15 | Gentex SHG24-15/75-C Horn/Strobe | 0 | 0.123
16 | Gentex SHG24-15/75-W Horn/Strobe | 0 | 0.123
17 | Gentex SHG24-15/75-Z Horn/Strobe | 0 | 0.123
18 | Gentex SHG24-30 Horn/Strobe | 0 | 0.123
19 | Gentex SHG24-30/75 Horn/Strobe | 0 | 0.172
20 | Gentex SHG24-60 Horn/Strobe | 0 | 0.145
21 | Gentex ST24-110 Strobe | 0 | 0.11
22 | Gentex ST24-15 Strobe | 0 | 0.047
23 | Gentex ST24-15/75 Strobe | 0 | 0.057
24 | Gentex ST24-30 Strobe | 0 | 0.057
25 | Gentex ST24-60 Strobe | 0 | 0.084
26 | Gentex ST24-75 Strobe | 0 | 0.086
27 | Silent Knight end of line relay EOL-1224RLY | 0.015 | 0.015
28 | System Sensor H12/24 Horn | 0 | 0.025
29 | System Sensor P24110 Horn/Strobe | 0 | 0.165
30 | System Sensor P241575 Horn/Strobe | 0 | 0.074
31 | System Sensor P2430 Horn/Strobe | 0 | 0.092
32 | System Sensor P2475 Horn/Strobe | 0 | 0.148
33 | System Sensor S2415 Strobe | 0 | 0.043
34 | System Sensor S241575 Strobe | 0 | 0.049
35 | System Sensor S2430 Strobe | 0 | 0.067
36 | System Sensor S2475 Strobe | 0 | 0.123
37 | System Sensor SS24110 Strobe | 0 | 0.14
38 | Wheelock AMT-24-IS-VFR Strobe Horn | 0 | 0.04
39 | Wheelock AMT-24-LSM-VFR Strobe Horn | 0 | 0.125
40 | Wheelock AS-24110-HFR Strobe Horn | 0 | 0.202
41 | Wheelock AS-241575-VFR Strobe Horn | 0 | 0.102
42 | Wheelock AS-2415-VFR Strobe Horn | 0 | 0.087
43 | Wheelock AS-2430-VFR Strobe Horn | 0 | 0.135
44 | Wheelock AS-2475-VFR Strobe Horn | 0 | 0.156
45 | Wheelock MIZ-24-R Mini-Horn | 0 | 0.012
46 | Wheelock MIZ-24-W Mini-Horn | 0 | 0.012
47 | User Defined
48 | User Defined
49 | User Defined
50 | User Defined
51 | User Defined
52 | User Defined
53 | User Defined
54 | User Defined
55 | User Defined
56 | User Defined
57 | User Defined
58 | User Defined
59 | User Defined
60 | User Defined
61 | User Defined
62 | User Defined
63 | User Defined
64 | User Defined
65 | User Defined
66 | User Defined
67 | User Defined
68 | User Defined
69 | User Defined
70 | User Defined
71 | User Defined
72 | User Defined
73 | User Defined
74 | User Defined
75 | User Defined
76 | User Defined
77 | User Defined
78 | User Defined
79 | User Defined
80 | User Defined
81 | User Defined
82 | User Defined
83 | User Defined
84 | User Defined
85 | User Defined
86 | User Defined
87 | User Defined
88 | User Defined
89 | User Defined
90 | User Defined
91 | User Defined
92 | User Defined
93 | User Defined
94 | User Defined
95 | User Defined
96 | User Defined
97 | User Defined
98 | User Defined
99 | User Defined
100 | User Defined
101 | User Defined
102 | User Defined
103 | User Defined
104 | User Defined
105 | User Defined
106 | User Defined
107 | User Defined
108 | User Defined
109 | User Defined
110 | User Defined
111 | User Defined
112 | User Defined
113 | User Defined
114 | User Defined
115 | User Defined
116 | User Defined
117 | User Defined
118 | User Defined
119 | User Defined
120 | User Defined
121 | User Defined
122 | User Defined
123 | User Defined
124 | User Defined
125 | User Defined
126 | User Defined
127 | User Defined
128 | User Defined
129 | User Defined
130 | User Defined
131 | User Defined
132 | User Defined
133 | User Defined
134 | User Defined
135 | User Defined
136 | User Defined
137 | User Defined
138 | User Defined
139 | User Defined
140 | User Defined
141 | User Defined
142 | User Defined
143 | User Defined
144 | User Defined
145 | User Defined
146 | User Defined
147 | User Defined
148 | User Defined
149 | User Defined
150 | User Defined
All of the devices shown in this table will appear as choices in the dropdown boxes used to configure each NAC circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.
Command Shortcuts

## Data (hidden)
Conductor Properties NEC Chap. 9
Item | Wire Type | Ohms Per 1000 ft.
1 | #12 Solid | 1.59
2 | #12 Stranded | 1.59
3 | #14 Solid | 2.52
4 | #14 Stranded | 2.52
5 | #16 Solid | 4.02
6 | #16 Stranded | 4.02
7 | #18 Solid | 6.39
8 | #18 Stranded | 6.39
Cell Links For The Wire Type Drop Down Boxes Associated With Each 5395
| 5395(1) | 5395(2) | 5395(3) | 5395(4) | 5395(5) | 5395(6) | 5395(7) | 5395(8)
1 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | bar: 5395(1) to 5395(8)
3 | bar: 5395(1) to 5395(8)
4 | bar: 5395(1) to 5395(8)
5 | bar: 5395(1) to 5395(8)
6 | bar: 5395(1) to 5395(8)
1 | 5395(1): Notification Appl Circuit
2 | 5395(1): Initiating Device Circuit
3 | 5395(1): Aux Power Circuit
| I/O1 | 1
| I/O2 | 1
| I/O3 | 1
| I/O4 | 1
| I/O5 | 1
| I/O6 | 1