## Power Supply Config
|  |  | Project Name: |  | Standby Hours: | 24
|  |  | Project ID: |  | Alarm Mins: | 15
|  |  | Prepared By: |  | Derating | 1.2
EVS-125W Calculations |  |  |  | Date:
Panel ID: | EVS-125W |  | Model: | EVS-125W Audio Amplifier
Location:
Ckt.# | Circuit Name | Qty | Current Draw
|  |  | Standby | Alarm
EVS-125W | EVS-125w Amplifier 25 Volts* |  | 0 | 0
EVS-CE4 | 4 Zone Expander |  | 0 | 0
Watts | Enter Number of Watts |  | N/A | 0
Total Standby Current (AMPS) |  |  | 0 | 0
Standby Time In Hours |  |  | 24 | 0.25
Total Standby AH Required |  |  | 0 | 0
Total Combined AH Required |  |  | 0
Multiply By The Derating Factor |  |  | 1.2
Minimum Battery AmpHours Required |  |  | 0
*The ECS-125W only operates on 25 VRMS

## Smokes
Device Database
ll of the devics shown in this table will appear as choices in the dropdown boxes used to configure each Initiating deice circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.

## Devices
Device Database
Notification Appliance Database
Item# | Device / Description | Current Draw In Amperes
|  | Standby | Alarm
1 | Unused
2 | Gentex GMH-24-X Horn | 0 | 0.038
3 | Gentex GX90-4 Horn | 0 | 0.015
4 | Gentex GX90S-4-15 Horn | 0 | 0.093
5 | Gentex GX90S-4-1575 Horn | 0 | 0.108
6 | Gentex GXS-4-1575 Strobe | 0 | 0.145
7 | Gentex HG124 Horn | 0 | 0.03
8 | Gentex HS24-110 Horn/Strobe | 0 | 0.14
9 | Gentex HS24-15 Horn/Strobe | 0 | 0.077
10 | Gentex HS24-15/75 Horn/Strobe | 0 | 0.087
11 | Gentex HS24-30 Horn/Strobe | 0 | 0.087
12 | Gentex HS24-60 Horn/Strobe | 0 | 0.114
13 | Gentex HS24-75 Horn/Strobe | 0 | 0.116
14 | Gentex SHG24-110 Horn/Strobe | 0 | 0.25
15 | Gentex SHG24-15/75-C Horn/Strobe | 0 | 0.123
16 | Gentex SHG24-15/75-W Horn/Strobe | 0 | 0.123
17 | Gentex SHG24-15/75-Z Horn/Strobe | 0 | 0.123
18 | Gentex SHG24-30 Horn/Strobe | 0 | 0.123
19 | Gentex SHG24-30/75 Horn/Strobe | 0 | 0.172
20 | Gentex SHG24-60 Horn/Strobe | 0 | 0.145
21 | Gentex ST24-110 Strobe | 0 | 0.11
22 | Gentex ST24-15 Strobe | 0 | 0.047
23 | Gentex ST24-15/75 Strobe | 0 | 0.057
24 | Gentex ST24-30 Strobe | 0 | 0.057
25 | Gentex ST24-60 Strobe | 0 | 0.084
26 | Gentex ST24-75 Strobe | 0 | 0.086
27 | Silent Knight EOL Relay EOL-1224RLY | 0.015 | 0.015
28 | System Sensor H12/24 Horn | 0 | 0.025
29 | System Sensor P24110 Horn/Strobe | 0 | 0.165
30 | System Sensor P241575 Horn/Strobe | 0 | 0.074
31 | System Sensor P2430 Horn/Strobe | 0 | 0.092
32 | System Sensor P2475 Horn/Strobe | 0 | 0.148
33 | System Sensor S2415 Strobe | 0 | 0.043
34 | System Sensor S241575 Strobe | 0 | 0.049
35 | System Sensor S2430 Strobe | 0 | 0.067
36 | System Sensor S2475 Strobe | 0 | 0.123
37 | System Sensor SS24110 Strobe | 0 | 0.14
38 | Wheelock AMT-24-IS-VFR Strobe Horn | 0 | 0.04
39 | Wheelock AMT-24-LSM-VFR Strobe Horn | 0 | 0.125
40 | Wheelock AS-24110-HFR Strobe Horn | 0 | 0.202
41 | Wheelock AS-241575-VFR Strobe Horn | 0 | 0.102
42 | Wheelock AS-2415-VFR Strobe Horn | 0 | 0.087
43 | Wheelock AS-2430-VFR Strobe Horn | 0 | 0.135
44 | Wheelock AS-2475-VFR Strobe Horn | 0 | 0.156
45 | Wheelock MIZ-24-R Mini-Horn | 0 | 0.012
46 | Wheelock MIZ-24-W Mini-Horn | 0 | 0.012
47 | User Defined
48 | User Defined
49 | User Defined
50 | User Defined
51 | User Defined
52 | User Defined
53 | User Defined
54 | User Defined
55 | User Defined
56 | User Defined
57 | User Defined
58 | User Defined
59 | User Defined
60 | User Defined
61 | User Defined
62 | User Defined
63 | User Defined
64 | User Defined
65 | User Defined
66 | User Defined
67 | User Defined
68 | User Defined
69 | User Defined
70 | User Defined
71 | User Defined
72 | User Defined
73 | User Defined
74 | User Defined
75 | User Defined
76 | User Defined
77 | User Defined
78 | User Defined
79 | User Defined
80 | User Defined
81 | User Defined
82 | User Defined
83 | User Defined
84 | User Defined
85 | User Defined
86 | User Defined
87 | User Defined
88 | User Defined
89 | User Defined
90 | User Defined
91 | User Defined
92 | User Defined
93 | User Defined
94 | User Defined
95 | User Defined
96 | User Defined
97 | User Defined
98 | User Defined
99 | User Defined
100 | User Defined
101 | User Defined
102 | User Defined
103 | User Defined
104 | User Defined
105 | User Defined
106 | User Defined
107 | User Defined
108 | User Defined
109 | User Defined
110 | User Defined
111 | User Defined
112 | User Defined
113 | User Defined
114 | User Defined
115 | User Defined
116 | User Defined
117 | User Defined
118 | User Defined
119 | User Defined
120 | User Defined
121 | User Defined
122 | User Defined
123 | User Defined
124 | User Defined
125 | User Defined
126 | User Defined
127 | User Defined
128 | User Defined
129 | User Defined
130 | User Defined
131 | User Defined
132 | User Defined
133 | User Defined
134 | User Defined
135 | User Defined
136 | User Defined
137 | User Defined
138 | User Defined
139 | User Defined
140 | User Defined
141 | User Defined
142 | User Defined
143 | User Defined
144 | User Defined
145 | User Defined
146 | User Defined
147 | User Defined
148 | User Defined
149 | User Defined
150 | User Defined
All of the devices shown in this table will appear as choices in the dropdown boxes used to configure each NAC circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.
Command Shortcuts

## Data (hidden)
Conductor Properties NEC Chap. 9
Item | Wire Type | Ohms Per 1000 ft.
1 | #12 Solid | 1.59
2 | #12 Stranded | 1.59
3 | #14 Solid | 2.52
4 | #14 Stranded | 2.52
5 | #16 Solid | 4.02
6 | #16 Stranded | 4.02
7 | #18 Solid | 6.39
8 | #18 Stranded | 6.39
Cell Links For The Wire Type Drop Down Boxes Associated With Each 5395
| 5395(1) | 5395(2) | 5395(3) | 5395(4) | 5395(5) | 5395(6) | 5395(7) | 5395(8)
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Aux | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1