## Instructions
Morley-IAS PL-1000
Step | Tab | Action
1 | Loop 1 Field Devices | Define the number of Devices present in your System, indicating it in column C near the respective device type.
2 | Loop 1 Field Devices | Insert the number of Isolators needed into cell D2
3 | Loop 1 Field Devices | Select the required loop length from the drop down menu in cell B1
4 | Loop 1 Field Devices | Select the Loop Cable Section in cell B2
5 | Loop 1 Field Devices | If the cable used is not standard, override the cable resistance in D1. If using a standard cable, leave blank
6 | Loop 2 Field Devices | Define the number of Devices present in your System, indicating it in column C near the respective device type.
7 | Loop 2 Field Devices | Insert the number of Isolators needed into cell D2
8 | Loop 2 Field Devices | Select the required loop length from the drop down menu in cell B1
9 | Loop 2 Field Devices | Select the Loop Cable Section in cell B2
10 | Loop 2 Field Devices | If the cable used is not standard, override the cable resistance in D1. If using a standard cable, leave blank
11 | PL-1000 | Insert the number and Stand-by / Alarm values for any conventional devices connected to the panels SND Outputs respectively in the cells C7, D7 & E7 and C9, D9 & E9.
12 | PL-1000 | Check cells C13 and C15 to verify that the maximum number of devices for each loop is inside the Loop Addresses Limits. In case not, please reduce the device quantity.
13 | PL-1000 | Check cells G17 and G19 to verify that the maximum current in Alarm for each loop is inside the Panel Power Supply Limits. In case not, please reduce the device load.
14 | PL-1000 | Check cells D21 to verify that your system is inside the Panel Power Supply Limits. In case not, please reduce the device load.
15 | PL-1000 | Check cells D26 to verify that your system is inside the Panel Battery Limits. In case not, please reduce the device load.
16 | PL-1000 | The number of isolators in D1 will add up to the total loop resistance, thus limiting the maximum current that can be drawn.
Note: The Loop Calculator takes into account the worst case scenario when an open circuit occurs in the loop in panel proximity, forcing the last device on the loop tp be powered from the other end of the circuit. In case System Limits are exceeded, please increase the cable section and/or decrease the number of Devices/Isolators (*).
(*) Number of Isolators must conform to the local regualtory framework

## Loop 1 Field Devices
Loop Length (m) max 1500 | 1500 | Cable resistance Override (Ohm)
Loop Cable Section (mm2) max. 2x2.5 | 1.5 | # Isolators | 0 | 0 |  | Totals (mA) | 0 | 0
Hardware Type | Device Type | Quantity | Individual Address Occupancy | Total Address Occupancy | Individual Stand-by Current (mA) | Individual Alarm Current (mA) | Total Stand-by Current (mA) | Total Alarm Current (mA)
Wireless | Wireless Gateway | 0 | 1 | 0 | 0.23 | 3.5 | 0 | 0
Wireless | Wireless Repeater | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireless Detector | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireless MCP | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireles Sounder | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireless Sounder Strobe | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireless Input Otput Module | 0 | 2 | 0 | 0 | 0 | 0 | 0
Detector | Smoke Sensor | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Thermal Sensor 58 deg C | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Thermal Sensor 78 deg C | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Thermal Sensor Rate-of-Rise | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Multi: Smoke and Thermal | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Multi: Smoke, Thermal and IR Sensor | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | High Sesitivity Smoke Detector | 0 | 1 | 0 | 0.3 | 1 | 0 | 0
Detector | Beam Detector | 0 | 1 | 0 | 2 | 8.5 | 0 | 0
Module New Range E | Input Module | 0 | 1 | 0 | 0.14 | 3.5 | 0 | 0
Module New Range E | Output Module | 0 | 1 | 0 | 0.16 | 7 | 0 | 0
Module New Range E | IO Unit (Ix2 Ox1) | 0 | 3 | 0 | 0.14 | 14 | 0 | 0
Module New Range E | IO Unit (Ix2) | 0 | 2 | 0 | 0.14 | 7 | 0 | 0
Module New Range E | Output Module 240V | 0 | 1 | 0 | 0.75 | 5.5 | 0 | 0
Module New Range E | Conventional Zone Module | 0 | 1 | 0 | 0.5 | 2.2 | 0 | 0
Module Old Range | Input Module | 0 | 1 | 0 | 0.2 | 3.5 | 0 | 0
Module Old Range | Output Module | 0 | 1 | 0 | 0.31 | 7 | 0 | 0
Module Old Range | IO Unit (Ix2 Ox1) | 0 | 3 | 0 | 0.2 | 14 | 0 | 0
Module Old Range | IO Unit (Ix2) | 0 | 2 | 0 | 0.2 | 7 | 0 | 0
Module Old Range | Output Module 240V | 0 | 1 | 0 | 0.75 | 5.5 | 0 | 0
Module Old Range | Conventional Zone Module | 0 | 1 | 0 | 0.5 | 2.2 | 0 | 0
Module Old Range | Mini Input Module | 0 | 1 | 0 | 0.11 | 3.5 | 0 | 0
Module Multiple I/O | 6 Output Relay | 0 | 6 | 0 | 1.49 | 36 | 0 | 0
Module Multiple I/O | 6 Output Controlled | 0 | 6 | 0 | 2.34 | 36 | 0 | 0
Module Multiple I/O | 10 Input | 0 | 10 | 0 | 3.5 | 60 | 0 | 0
Module Multiple I/O | 6 Conventional Zones | 0 | 6 | 0 | 2.04 | 40 | 0 | 0
Manual Call Point | Indoor MCP | 0 | 1 | 0 | 0.12 | 7 | 0 | 0
Manual Call Point | Outdoor MCP | 0 | 1 | 0 | 0.12 | 7 | 0 | 0
Audio Visual Devices | Sounder Wall Mounted | 0 | 1 | 0 | 0.225 | 11.4 | 0 | 0
Audio Visual Devices | Sounder Strobe RED Wall Mounted | 0 | 1 | 0 | 0.225 | 14.5 | 0 | 0
Audio Visual Devices | Strobe Wall Mounted - VAD | 0 | 1 | 0 | 0.225 | 5.4 | 0 | 0
Audio Visual Devices | Sounder Base | 0 | 1 | 0 | 0.225 | 10.5 | 0 | 0
Audio Visual Devices | Strobe Base C Class | 0 | 1 | 0 | 0.15 | 15 | 0 | 0
Audio Visual Devices | Sounder Strobe RED Base | 0 | 1 | 0 | 0.225 | 3.5 | 0 | 0
Audio Visual Devices | Sounder Strobe WHITE Base O Calss | 0 | 1 | 0 | 0.45 | 10 | 0 | 0
Audio Visual Devices | Sounder Strobe Base C Class High-Power HIGH Setup | 0 | 1 | 0 | 0.15 | 27 | 0 | 0
Audio Visual Devices | Sounder Strobe Base C Class High-Power LOW Setup | 0 | 1 | 0 | 0.15 | 18.5 | 0 | 0
Audio Visual Devices | Sounder Strobe Base C Class High-Power Legacy Setup | 0 | 1 | 0 | 0.15 | 8 | 0 | 0

## Loop 2 Field Devices
Loop Length (m) max 1500 | 1500 | Cable resistance Override (Ohm)
Loop Cable Section (mm2) max. 2x2.5 | 1.5 | #Isolators | 0 | 0 |  | Totals (mA) | 0 | 0
Hardware Type | Device Type | Quantity | Individual Address Occupancy | Total Address Occupancy | Individual Stand-by Current (mA) | Individual Alarm Current (mA) | Total Stand-by Current (mA) | Total Alarm Current (mA)
Wireless | Wireless Gateway | 0 | 1 | 0 | 0.23 | 3.5 | 0 | 0
Wireless | Wireless Repeater | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireless Detector | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireless MCP | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireles Sounder | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireless Sounder Strobe | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireless Input Otput Module | 0 | 2 | 0 | 0 | 0 | 0 | 0
Detector | Smoke Sensor | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Thermal Sensor 58 deg C | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Thermal Sensor 78 deg C | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Thermal Sensor Rate-of-Rise | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Multi: Smoke and Thermal | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Multi: Smoke, Thermal and IR Sensor | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | High Sesitivity Smoke Detector | 0 | 1 | 0 | 0.3 | 1 | 0 | 0
Detector | Beam Detector | 0 | 1 | 0 | 2 | 8.5 | 0 | 0
Module New Range E | Input Module | 0 | 1 | 0 | 0.14 | 3.5 | 0 | 0
Module New Range E | Output Module | 0 | 1 | 0 | 0.16 | 7 | 0 | 0
Module New Range E | IO Unit (Ix2 Ox1) | 0 | 3 | 0 | 0.14 | 14 | 0 | 0
Module New Range E | IO Unit (Ix2) | 0 | 2 | 0 | 0.14 | 7 | 0 | 0
Module New Range E | Output Module 240V | 0 | 1 | 0 | 0.75 | 5.5 | 0 | 0
Module New Range E | Conventional Zone Module | 0 | 1 | 0 | 0.5 | 2.2 | 0 | 0
Module Old Range | Input Module | 0 | 1 | 0 | 0.2 | 3.5 | 0 | 0
Module Old Range | Output Module | 0 | 1 | 0 | 0.31 | 7 | 0 | 0
Module Old Range | IO Unit (Ix2 Ox1) | 0 | 3 | 0 | 0.2 | 14 | 0 | 0
Module Old Range | IO Unit (Ix2) | 0 | 2 | 0 | 0.2 | 7 | 0 | 0
Module Old Range | Output Module 240V | 0 | 1 | 0 | 0.75 | 5.5 | 0 | 0
Module Old Range | Conventional Zone Module | 0 | 1 | 0 | 0.5 | 2.2 | 0 | 0
Module Old Range | Mini Input Module | 0 | 1 | 0 | 0.11 | 3.5 | 0 | 0
Module Multiple I/O | 6 Output Relay | 0 | 6 | 0 | 1.49 | 36 | 0 | 0
Module Multiple I/O | 6 Output Controlled | 0 | 6 | 0 | 2.34 | 36 | 0 | 0
Module Multiple I/O | 10 Input | 0 | 10 | 0 | 3.5 | 60 | 0 | 0
Module Multiple I/O | 6 Conventional Zones | 0 | 6 | 0 | 2.04 | 40 | 0 | 0
Manual Call Point | Indoor MCP | 0 | 1 | 0 | 0.12 | 7 | 0 | 0
Manual Call Point | Outdoor MCP | 0 | 1 | 0 | 0.12 | 7 | 0 | 0
Audio Visual Devices | Sounder Wall Mounted | 0 | 1 | 0 | 0.225 | 11.4 | 0 | 0
Audio Visual Devices | Sounder Strobe RED Wall Mounted | 0 | 1 | 0 | 0.225 | 14.5 | 0 | 0
Audio Visual Devices | Strobe Wall Mounted - VAD | 0 | 1 | 0 | 0.225 | 5.4 | 0 | 0
Audio Visual Devices | Sounder Base | 0 | 1 | 0 | 0.225 | 10.5 | 0 | 0
Audio Visual Devices | Strobe Base C Class | 0 | 1 | 0 | 0.15 | 15 | 0 | 0
Audio Visual Devices | Sounder Strobe RED Base | 0 | 1 | 0 | 0.225 | 3.5 | 0 | 0
Audio Visual Devices | Sounder Strobe WHITE Base O Calss | 0 | 1 | 0 | 0.45 | 10 | 0 | 0
Audio Visual Devices | Sounder Strobe Base C Class High-Power HIGH Setup | 0 | 1 | 0 | 0.15 | 27 | 0 | 0
Audio Visual Devices | Sounder Strobe Base C Class High-Power LOW Setup | 0 | 1 | 0 | 0.15 | 18.5 | 0 | 0
Audio Visual Devices | Sounder Strobe Base C Class High-Power Legacy Setup | 0 | 1 | 0 | 0.15 | 8 | 0 | 0

## Loop_Lenght_Section_Selection (hidden)
100 | 0.5 | Cable Resistance |  | Max Allowed Voltage Drop (V) |  | Isolator resistance (Ohm)
200 | 1 | Loop 1 | Loop 2 | 9 |  | 0.17
300 | 1.5 | 17.8571 | 17.8571
400 | 2.5
500
600
700 |  |  |  | Max Allowed Current Loop 1 | 252
800 |  |  |  | Max Allowed Current Loop 2 | 252
900
1000
1100 |  |  |  | Battery capacity (Ah) | 7
1200
1300
1400
1500 |  |  |  | LED current (mA) | 6
|  |  |  | Number of LEDs max per loop | 5
|  |  |  | Extra current Isolator activated (mA) | 15

## PL-1000
BATTERY CALCULATOR TOOL MORLEY PL-1000
Device | Quantity | Unit Stand By Absorption (mA) | Total Stand By Absorption (mA) | Unit Alarm Absorption (mA) | Total Alarm Absorption (mA)
Display & Main Board - FIXED VALUES |  |  | 70 |  | 112.5
Optional Loop Card PL-LIB01 - FIXED VALUES | 1 | 50 | 50 | 50 | 50
Alarm SND Out 1 (Max 250 mA) | 1 | 0 | 0 | 45 | 45
Alarm SND Out 2 (Max 250 mA) | 1 | 0 | 0 | 45 | 45
Total Stand-by and Alarm Currents |  |  | 120 |  | 252.5
Total Loop 1 Devices Installed (Max 159 Detectors + 159 I/O Modules) | 0 |  | 0
Total Loop 2 Devices Installed (Max 159 Detectors + 159 I/O Modules) | 0 |  | 0
Total Loop 1 Audio Visual Loop Powered Devices in Alarm | 0 |  |  |  | 0
Total Loop 2 Audio Visual Loop Powered Devices in Alarm | 0 |  |  |  | 0
Total Loop 1 Absorption |  | In System Limits | 0
Total Loop 2 Absorption |  | In System Limits | 0
Total Loop 1 and Loop 2 Absorption |  |  | 0 |  | 0
Total System Absorption |  | In PSU Limits | 120 |  | 252.5
Stand By (h) / Value in Ah | 24 |  | 2.88
Alarm Condition (h) / Value in Ah | 0.5 |  | 0.13
Discharge Factor | 25% |  | 0.76
Total Battery Capacity (A) | Check | In Battery Limits | 3.8
Threshold Current In Panel for Loop 1 | 45
Threshold Current In Panel for Loop 2 | 45
Note on G3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Includes absorbtion of buzzer and alarm led both on and 5 Point Detector Contemporary in Alarm Condition.
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry - Max 1 Card
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on F7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on F9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry