## Instructions
Morley LT-32
Step | Tab | Action
1 | Field Devices | Define the number of Devices present in your System, indicating it in column C near the respective device type.
2 | LT-32 | Insert the number and Stand-by / Alarm values for any conventional devices connected to the panels SND Outputs respectively in the cells B5-B6, C5-C6, E5-E6.
3 | LT-32 | Check cell B10 to verify that the maximum number of system devices is inside the Panel limits.
4 | LT-32 | Check cells C16 to verify that your system is inside the Panel Power Supply Limits. In case not, please reduce the device load.
5 | LT-32 | Check cells C24 to verify that your system is inside the Panel Battery Limits. In case not, please reduce the device load.
Morley LT-159
Step | Tab | Action
1 | Field Devices | Define the number of Devices present in your System, indicating it in column C near the respective device type.
2 | LT-159 | Insert the number and Stand-by / Alarm values for any conventional devices connected to the panels SND Outputs respectively in the cells B5, C5, E5.
3 | LT-159 | Check cell B9 to verify that the maximum number of system devices is inside the Panel limits.
4 | LT-159 | Check cells C15 to verify that your system is inside the Panel Power Supply Limits. In case not, please reduce the device load.
5 | LT-159 | Check cells C23 to verify that your system is inside the Panel Battery Limits. In case not, please reduce the device load.

## Field Devices
|  |  | Total Addresses | 6 |  | Totals (mA) | 0.9 | 44
Hardware Type | Device Type | Quantity | Individual Address Occupancy | Total Address Occupancy | Individual Stand-by Current (mA) | Individual Alarm Current (mA) | Total Stand-by Current (mA) | Total Alarm Current (mA)
Wireless | Wireless Gateway | 0 | 1 | 0 | 0.23 | 3.5 | 0 | 0
Wireless | Wireless Detector | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireless MCP | 2 | 1 | 2 | 0 | 0 | 0 | 0
Wireless | Wireles Sounder | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireless Sounder Strobe | 0 | 1 | 0 | 0 | 0 | 0 | 0
Wireless | Wireless Input Otput Module | 0 | 2 | 0 | 0 | 0 | 0 | 0
Detector | Smoke Sensor | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Thermal Sensor 58 deg C | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Thermal Sensor 78 deg C | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Thermal Sensor Rate-of-Rise | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Multi: Smoke and Thermal | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Detector | Multi: Smoke, Thermal and IR Sensor | 0 | 1 | 0 | 0.3 | 3.5 | 0 | 0
Module New Range E | Input Module | 0 | 1 | 0 | 0.14 | 3.5 | 0 | 0
Module New Range E | Output Module | 0 | 1 | 0 | 0.16 | 7 | 0 | 0
Module New Range E | IO Unit (Ix2 Ox1) | 0 | 3 | 0 | 0.16 | 4.5 | 0 | 0
Module New Range E | IO Unit (Ix2) | 0 | 2 | 0 | 0.14 | 7 | 0 | 0
Module New Range E | Output Module 240V | 0 | 1 | 0 | 0.75 | 5.5 | 0 | 0
Module New Range E | Conventional Zone Module | 0 | 1 | 0 | 0.5 | 2.2 | 0 | 0
Module Old Range | Input Module | 0 | 1 | 0 | 0.5 | 3.5 | 0 | 0
Module Old Range | Output Module | 0 | 1 | 0 | 0.31 | 7 | 0 | 0
Module Old Range | IO Unit (Ix2 Ox1) | 0 | 3 | 0 | 0.66 | 7.3 | 0 | 0
Module Old Range | IO Unit (Ix2) | 0 | 2 | 0 | 0.2 | 7 | 0 | 0
Module Old Range | Output Module 240V | 0 | 1 | 0 | 0.75 | 5.5 | 0 | 0
Module Old Range | Conventional Zone Module | 0 | 1 | 0 | 0.5 | 2.2 | 0 | 0
Module Old Range | Mini Input Module | 0 | 1 | 0 | 0.11 | 3.5 | 0 | 0
Module Multiple I/O | 6 Output Relay | 0 | 6 | 0 | 1.49 | 36 | 0 | 0
Module Multiple I/O | 6 Output Controlled | 0 | 6 | 0 | 2.34 | 36 | 0 | 0
Module Multiple I/O | 10 Input | 0 | 10 | 0 | 3.5 | 60 | 0 | 0
Module Multiple I/O | 6 Conventional Zones | 0 | 6 | 0 | 2.04 | 40 | 0 | 0
Manual Call Point | Indoor MCP | 0 | 1 | 0 | 0.12 | 7 | 0 | 0
Manual Call Point | Outdoor MCP | 0 | 1 | 0 | 0.12 | 7 | 0 | 0
Audio Visual Devices | Sounder Wall Mounted | 4 | 1 | 4 | 0.225 | 11 | 0.9 | 44
Audio Visual Devices | Sounder Strobe Wall Mount High EN54-23 W Class | 0 | 1 | 0 | 0.13 | 23.8 | 0 | 0
Audio Visual Devices | Sounder Strobe Wall Mount Med EN54-23 W Class | 0 | 1 | 0 | 0.13 | 19.8 | 0 | 0
Audio Visual Devices | Sounder Strobe Wall Mount Low EN54-23 W Class | 0 | 1 | 0 | 0.13 | 14.8 | 0 | 0
Audio Visual Devices | Strobe only Wall Mount Low EN54-23 W Class | 0 | 1 | 0 | 0.13 | 11 | 0 | 0
Audio Visual Devices | Sounder Strobe RED Wall Mounted | 0 | 1 | 0 | 0.225 | 14.5 | 0 | 0
Audio Visual Devices | Strobe Wall Mounted - VAD | 0 | 1 | 0 | 0.225 | 5.4 | 0 | 0
Audio Visual Devices | Strobe only Wall Mount Low EN54-23 W Class | 0 | 1 | 0 | 0.13 | 11 | 0 | 0
Audio Visual Devices | Sounder Base | 0 | 1 | 0 | 0.225 | 10.5 | 0 | 0
Audio Visual Devices | Strobe Base C Class | 0 | 1 | 0 | 0.15 | 15 | 0 | 0
Audio Visual Devices | Sounder Strobe RED Base | 0 | 1 | 0 | 0.225 | 3.5 | 0 | 0
Audio Visual Devices | Sounder Strobe WHITE Base O Calss | 0 | 1 | 0 | 0.45 | 10 | 0 | 0
Audio Visual Devices | Sounder Strobe Base C Class High-Power HIGH Setup | 0 | 1 | 0 | 0.15 | 27 | 0 | 0
Audio Visual Devices | Sounder Strobe Base C Class High-Power LOW Setup | 0 | 1 | 0 | 0.15 | 18.5 | 0 | 0
Audio Visual Devices | Sounder Strobe Base C Class High-Power Legacy Setup | 0 | 1 | 0 | 0.15 | 8 | 0 | 0

## LT-32
BATTERY CALCULATOR TOOL MORLEY LT-32
Device | Quantity | Unit Stand By Absorption (mA) | Total Stand By Absorption (mA) | Unit Alarm Absorption (mA) | Total Alarm Absorption (mA)
Display & Main Board - FIXED VALUES |  |  | 45 |  | 47
Alarm Out 1 (Max 50 mA) | 1 | 0 | 0 | 50 | 50
Alarm Out 2 (Max 50 mA) (NPX Open loop only) | 1 | 0 | 0 | 50 | 50
Total Alarm Current |  |  |  |  | 147
Total Loop Devices Installed (Max 32 Devices) | 6 |  | 0.9 |  | 44
Max Number Devices Contemporary in Alarm with LED On | 5 |  |  | 3.5 | 17.5
Number Audio Visual Loop Powered Devices in Alarm | 4 |  |  |  | 44
Total Loop Absorption |  | 62.4
Total System Absorption | Check | In PSU Limits | 45.9 |  | 208.5
Average System Batteries Voltage (V) - FIXED VALUES |  |  | 7.5
Internal 20 V Voltage (V) - FIXED VALUES |  |  | 19
Stand By (h) | 24 |  | 1135
Alarm Condition (h) | 0.5 |  | 152
Discharge Factor | 25% |  | 322
Total Battery Capacity (mA) | Check | In Battery Limits | 1609
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on D5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on F5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on D6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on F6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Limited to 5 Devices

## LT-159
BATTERY CALCULATOR TOOL MORLEY LT-159
Device | Quantity | Unit Stand By Absorption (mA) | Total Stand By Absorption (mA) | Unit Alarm Absorption (mA) | Total Alarm Absorption (mA)
Display & Main Board - FIXED VALUES |  |  | 45 |  | 47
Alarm Out 1 (Max 50 mA) | 1 | 0 | 0 | 50 | 50
Total Alarm Current |  |  |  |  | 97
Total Loop Devices Installed (Max 159 Devices) | 6 |  | 0.9 |  | 44
Max Number Devices Contemporary in Alarm with LED On | 5 |  |  | 3.5 | 17.5
Number Audio Visual Loop Powered Devices in Alarm | 4 |  |  |  | 44
Total Loop Absorption |  | 62.4
Total System Absorption | Check | In PSU Limits | 45.9 |  | 158.5
Average System Batteries Voltage (V) - FIXED VALUES |  |  | 7.5
Internal 20 V Voltage (V) - FIXED VALUES |  |  | 19
Stand By (h) | 24 |  | 1135
Alarm Condition (h) | 0.5 |  | 127
Discharge Factor | 25% |  | 316
Total Battery Capacity (mA) | Check | In Battery Limits | 1578
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on D5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on F5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manual Entry
Note on C11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Limited to 5 Devices