STANLEY “SCSS–700” FIRE ALARM

CONTROL COMMUNICATOR SYSTEM

ENGINEER/ARCHITECT SPECIFICATION

## SECTION ONE: GENERAL

### 1.1	Scope

This specification document provides the requirements for the installation, programming 	and configuration of a complete Stanley SCSS-700 digital protocol analog addressable fire alarm system. This system shall include, but not be limited to, system cabinet, power supply, built in Signaling Line Circuit (SLC), 160 character LCD annunciator, eight programmable Flexputs, built in dual line digital communicator associated peripheral devices, batteries, wiring, conduit and other relevant components and accessories required to furnish a complete and operational Life Safety System.  SCSS-700 has the interconnection capability for up to 8 panels. The system has two modes of operation, multiple panels covering one larger building, or multiple independent buildings.  SCSS-700ND is used in a networked system where at least one SCSS-700 is in the system. It is the same as an SCSS-700 without the display.

### 1.2	Work Included

#### 1.2.1	General Requirements

The contractor shall furnish and install a complete 24 VDC, electrically supervised, analog addressable fire alarm system as specified herein and indicated on the drawings. The system shall include but not be limited to all control panels, power supplies, initiating devices, audible and visual notification appliances, alarm devices, and all accessories required to provide a complete operating fire alarm system.

#### 1.2.2	Listings

All fire alarm system equipment shall be listed for it’s intended purpose and be compatibility listed to assure the integrity of the complete system.

### 1.3	Standards

The fire alarm equipment and installation shall comply with the current provisions of the following standards and shall be listed for it’s intended purpose and be compatibility listed to insure integrity of the complete system.

#### 1.3.1	National Electric Code, Article 760

#### National Fire Protection Association Standards:

NFPA 70		National Electrical Code

NFPA 72		National Fire Alarm Code

NFPA 101 		Life Safety Code

#### Local and State Building Codes

BOCA, National Building Code, Mechanical Code, Fire Prevention Code

#### 1.3.4	Local Authorities Having Jurisdiction

#### 1.3.5	Underwriters Laboratories Inc.

All equipment shall be approved by Underwriters Laboratories, Inc. for it’s intended purpose, listed as power limited by Underwriters Laboratories, Inc., for the following standards as applicable:

UL 864 UOJZ 	Control units for Fire Protective Signaling Systems

Local Signaling Unit

Central Station Signaling Protected Premises Unit

Remote Signaling Protected Premises Unit.

UL 268 	Smoke Detectors for Fire Protective Signaling systems.

UL 268A 	Smoke Detectors for duct applications

UL 217		Smoke Detectors for Single Stations

UL 521 	Heat Detectors for Fire Protective Signaling systems.

UL 228 	Door Holders for Fire Protective Signaling systems.

UL 464 	Audible Signaling appliances

UL 1638 	Visual Signaling appliances

UL 38	 	Manually Activated Signaling Boxes

UL 346 	Waterflow indicators for Fire Protective Signaling systems.

UL 1481 	Power Supplies for Fire Protective Signaling systems.

#### 1.3.6	Americans with Disabilities Act (ADA).

All visual Notification appliances and manual pull stations shall comply with the requirements of the Americans with Disabilities Act.

  - General Requirements

    - Manufacturers/Distributors Services:

      - The following supervision shall be provided by a factory trained service technician. The technician shall be trained and shall have a minimum of two (2) years of service experience in the fire alarm industry. The technicians name shall appear on equipment submittals and a copy of his manufactures trained shall be sent to the project engineer. The technician shall be responsible for the following items:

- A pre installation visit to the job site to review equipment submittals and to verify the method by which the system is to be wired.

- During the installation the certified technician shall be on site or make periodic visits to verify installation and wiring of the system. He shall also supervise the completion of conduit rough, wires pulled into conduit and wiring rough, and ready for trim.

- Upon completion of wiring, final checkout and certification of the system shall be made under the supervision of this technician.

- At the time of the formal checkout, technician shall give operational instructions to the owner and or his representative on the system.

#### 1.4.2	Submittals

The contractor shall submit three (3) complete sets of documentation within thirty (30) calendar days after award of the purchase order.  Indicated in the document will be the type, size, rating, style, catalog number, manufacturers’ names, photos, and /or catalog data sheets for all items proposed to meet these specifications.  The proposed equipment 	shall be subject to the approval of the Architect/Engineer and no equipment shall be ordered or installed on the premises without that approval.

NOTE: DOCUMENTATION - Submittal of shop drawings shall contain at least three (3) copies of original manufacturer specification and installation instruction sheets. Subsequent information may be copies. All equipment and devices on the shop drawings to be furnished under this contract shall be clearly marked in the specification sheets.

Suppliers’ qualifications shall be submitted indicating years in business, service policies, 	warranty definitions, NICET certification, and completion of factory training program and a list of similar installations.

Contractor qualifications shall be supplied indicating years in business and prior experience with installations that include the type of equipment that is to be supplied.

The contractor shall provide hourly Service Rates, performed by a factory trained technician for this installed Life Safety System with the submittal.  Proof of training and authorization shall be included with the submittal.  These hourly service rates shall be guaranteed for a 1-year period.

#### 1.4.2	Contract close-out Submittals

Deliver two (2) copies of the following to the owner’s representative within Thirty (30) days of system acceptance.  The closeout submittals shall include:

- Installation and Programming manuals for the installed Life Safety System.

- Point to point diagrams of the entire Life Safety System as installed.  This shall include all connected Smoke Detectors and addressable field modules.

3-	All drawings must reflect device address as verified in the presence of the 			engineer and/or end user.

#### 1.4.3	Warranty

Warranty all materials, installation and workmanship for a one (1) year period, unless otherwise specified.  A copy of the manufacturer warranty shall be provided with the close out documentation.

#### 1.4.4	Products

This Life Safety System Specification must be conformed to in its entirety to ensure that 	the installed and programmed Life Safety System will accommodate all of the requirements and operations required by the building owner.  Any specified item or operational feature not specifically addressed prior to the bid date will be required to be met without exception.

Submission of product purported to be equal to those specified herein will be considered as possible substitutes only when all of the following requirements have been met:

- Any deviation from the equipment, operations, methods, design or other criteria specified herein must be submitted in detail to the specifying Architect or Engineer a minimum of ten (10) working days prior to the scheduled submission of bids. Each deviation from the operation detailed in these specifications must be documented in detail, including page number and section number, which list the system function for which the substitution is being proposed.

- A complete list of such substituted products with three (3) copies of working drawings thereof shall be submitted to the approved Architect and/or Consulting Engineer not less than ten (10) working days prior to the scheduled submission of bids.

3-	The contractor or substitute bidder shall functionally demonstrate that the 				proposed substitute products are in fact equal in quality and performance to those 			specified herein.

#### General Equipment and Materials Requirements

All equipment furnished for this project shall be new and unused.  All components shall be designed for uninterrupted duty.  All equipment, materials, accessories, devices and other facilities covered by this specification or noted on the contract drawings and installation specification shall be best suited for the intended use and shall be provided by a single manufacturer.  If any of the equipment provided under this specification is provided by different manufacturers, then that equipment shall be “Listed” as to its compatibility by Underwriters Laboratories (UL), if such compatibility is required by UL standards.

#### 1.4.6	Satisfying the Entire Intent of these Specifications

It is the contractor’s responsibility to meet the entire intent of these specifications.

Deviations from the specified items shall be at the risk of the contractor until the date of final acceptance by the architect, engineer, and owner’s representative.

All costs for removal, relocation, or replacement of a substituted item shall be at the risk of the electrical contractor.

## SECTION TWO: SPECIFICATIONS

### 2.1	General

#### 2.1.1	Control Panel

The fire alarm control panel (FACP) shall be the Stanley SCSS-700 analog addressable control panel.  The FACP must have a 9 amp power supply and be capable of expansion to a minimum of 45 total amps via bus connected expander modules that supervise low battery, loss off AC and loss of communication.

The FACP must have Day/Night sensitivity capabilities on detectors and be capable of supporting 159 detectors and 159 analog addressable modules and expandable to a maximum of 636 analog addressable points per FACP.  This shall be accomplished via a maximum of 63 signaling line circuits (SLC) capable of supporting up to 159 detectors and 159 addressable module devices each.  The communication protocol on the SLC loop must be digital.

The FACP must be capable of being networked to create a virtual system that is larger than 636

addressable points. The FACP network must support up to eight FACPs on the network providing a maximum addressable point capacity of 5,088 points (636 x 8 = 5,088).

The FACP must support a minimum of eight programmable “Flexputs”.  The panel must have a built in 160 character LCD annunciator with the capability of having a minimum of an additional eight supervised remote annunciators connected in the field.

The FACP must have a built in UL approved digital communicator.  The communicator must allow local and remote up/downloading of system operating options, event history, and detector sensitivity data.

The FACP must automatically test the smoke detectors in compliance with NFPA standards to ensure that they are within listed sensitivity parameters and be listed with Underwriters Laboratories for this purpose.

The FACP must compensate for the accumulation of contaminants that affect detector sensitivity.  The FACP must have day/night sensitivity adjustments, maintenance alert feature (differentiated from trouble condition), detector sensitivity selection, auto-programming mode (Jumpstart) and the ability to upgrade the core operating software on site or over the telephone.

The FACP shall have a Jumpstart feature that can automatically enroll all properly connected accessories into a functional system within 60 seconds of powering up the panel.  Panels that do not have these capabilities will not be accepted.

The main communication bus ( S-Bus RS485 ) shall be capable of class A or class B configuration with a total Bus length of 6,000 feet.

#### 2.1.2	System Wiring

The Signaling Line Circuit (SLC) and Data Communication Bus (S-BUS) shall be wired with standard NEC 760 compliant wiring, no twisted, shielded or mid capacitance wiring is required for standard installations.  All FACP screw terminals shall be capable of accepting 12-18 AWG wire. All system wiring shall be in accordance with the requirements of NFPA 70, the National Electrical Code (NEC) and also comply with article 760 of the NEC.

2.1.3	Signaling Line Circuits

Each SLC shall be capable of a wiring distance of 10,000 feet from the SLC driver module (5815XL) and be capable of supporting 159 detectors and 159 addressable module devices.  The communication protocol to SLC devices must be digital.  Any SLC loop device, which goes into alarm, must interrupt the polling cycle for priority response from the FACP.  The FACP must respond consistently to a device that goes into alarm on an SLC in under 10 seconds. The auxiliary 5815XL SLC loop module must be capable of being located up to 6000 feet from the FACP on an RS-485 bus, which is separate from the SLC bus. The SLC shall be capable of functioning in a class A or class B configuration.

#### 2.1.4	SLC loop devices

Devices supported must include analog photoelectric, analog heat detectors, addressable input modules, relay output modules or addressable notification modules. There is to be no limit to the number of any particular device type up to the maximum of 159 detectors and 159 addressable modules that can be connected to the SLC.

#### 2.1.5	Analog detector functions

The products of combustion detectors must communicate analog values using a digital 		protocol to the control panel for the following functions:

Automatic compliance with NFPA 72 standards for detector sensitivity testing

Drift compensation to assure detector is operating correctly

Maintenance alert when a detector nears the trouble condition

Trouble alert when a detector is out of tolerance

Alert control panel of analog values that indicate fire.

#### 2.1.6	Sensitivity function

The FACP shall have the ability to set three different sensitivity levels.  A zone can be programmed to a day and a night sensitivity value.  The day/night schedule shall allow for 16 holiday dates that are user programmable to allow the FACP to respond at the night level on those days.

#### 2.1.7	Programmable Flexputs

The FACP shall support eight programmable Flexput circuits that are capable of being programmed as supervised reverse polarity notification circuits or supervised auxiliary power circuits that can be programmed as continuous, resettable or door holder power.  The circuits shall also be programmable as input circuits in class A or B configurations to support dry contact or compatible two wire smoke detectors.

    - Addressable Control Module

The contractor shall furnish and install where indicated on the plans, addressable Control modules, Fire-Lite Model CMF-300. The modules shall be U.L. listed compatible with Stanley’s SCSS-700 fire alarm control panel. The Control module must provide one class A (Style Z) or class B (Style Y) notification output with one auxiliary power input. The Control module must be suitable for mounting in a standard 4 square electrical box and must include a plastic cover plate. The Control module must provide an LED that is visible from the outside of the cover plate. The Control module must be fully programmable for such applications as required by the installation. The CMF-300 shall reside on the SLC loop and can be placed up to 10,000ft. from the control or 5815XL SLC loop module.

#### 2.1.8	Annunciators

The main control must have a built in annunciator with a 160-character LCD display and feature LED’s for General alarm, Supervisory, System trouble, System Silence and Power.  When in the normal condition the LCD shall display time and date based on a 200 year clock which is capable of automatic daylight savings time adjustments.  All controls and programming keys are silicone mechanical type with tactile and audible feedback.  Keys have a travel of .040 in..  No membrane style buttons will be permissible. The annunciator must be able to silence and reset alarms through the use of a keypad entered code.  The annunciators must have twenty levels of user codes that will allow the limitation of operating system programming to authorized individuals.

#### 2.1.9	Remote Annunciators

The fire system shall be capable of supporting a minimum of eight remote annunciators.  LCD Remote annunciator Model SCSS-700ANN shall have the same control and display layout so that they match identically the built in annunciator. Remote annunciators shall have the same functionality and operation as the built in annunciator. All annunciators must have 160-character LCD displays and must feature five LED’s for general alarm, supervisory, system trouble, system silence, and system power. All controls and programming keys are silicone mechanical type with tactical and audible feedback. Keys shall have a travel of .040 inches. No membrane style buttons will be permitted.

The annunciator must be able to silence and reset alarms through the use of a code entered on the annunciator keypad. The annunciator must have twenty levels of user codes that will limit the operating system programming to authorized individuals. The control panel must allow all annunciators to accommodate multiple users input simultaneously. Remote annunciators shall be capable of operating at a distance of 6000 feet from the main control panel on unshielded non-twisted cable.

2.1.10 	The fire system shall be able to support a minimum of eight I/O modules (5880) that shall be used to drive remote LED graphic style displays and accommodate up to eight dry contact type switch inputs.  The I/O modules shall each drive up to 40 LEDs without requiring external power connections.  The I/O module inputs shall be supervised and be suitable for alarm and trouble circuits as well as reset and silence switches.  The system shall also support up to 40 LED drivers that reside on the two-wire SLC loop.  These driver boards shall contain 80 LED outputs that are powered by an external power source.

#### 2.1.11	Serial/Parallel interface

The fire system shall be capable of supporting up to two serial / parallel interfaces (5824) that are capable of driving standard computer style printers.  The interface shall be programmable as to what information is sent to it and shall include the ability to print out Detector Status by point, Event History by point and System Programming.

#### 2.1.12	Digital Communicator

The digital communicator must be an integral part of the control panel and be capable of reporting all zones or points of alarm, supervisory, and trouble as well as all system status information such as loss of AC, low battery, ground fault, loss of supervision to any remote devices with individual and distinct messages to a central station or remote station.  The communicator must also be capable of  up/downloading of all system programming options, Event history and Sensitivity compliance information to a PC on site or at a remote location.

The communicator shall have an answering machine bypass feature that will allow the panel to respond to communication even on phone lines that have other communication equipment present.  The communicator must be capable of reporting via SIA and Contact ID formats.  The communicator shall have a delayed AC loss report function which will provide a programmable report delay.  No controls that use External modems for remote programming and diagnostics shall be accepted.

#### 2.1.13	Dry Contacts

The FACP will have three form “C” dry contacts, one will be dedicated to trouble conditions, the other two will be programmable for alarm, trouble, sprinkler supervisory, notification, pre-alarm, waterflow, manual pull, aux. 1 or aux. 2.  The trouble contact shall be normal in an electrically energized state so that any total power loss (AC and Backup) will cause a trouble condition.  In the event that the Microprocessor on the FACP fails the trouble contacts shall also indicate a trouble condition.

#### 2.1.14	Ground Fault Detection

A ground fault detection circuit, to detect positive and negative grounds on all field wiring. The ground fault detector shall operate the general trouble devices as specified but shall not cause an alarm to be sounded. Ground fault will not interfere with the normal operation, such as alarm, or other trouble conditions.

#### 2.1.15	Over current Protection

All low voltage circuits will be protected by microprocessor controlled power limiting or have a self restoring polyswitches for the following: smoke detector power, main power supply, indicating appliance circuits, battery standby power and auxiliary output.

#### 2.1.16	Test Functions

A “Lamp Test” or “Indicator Test” mode shall be a standard feature of the fire alarm control panel and shall test all LED’s and the LCD display on the main panel and remote annunciators.

A “Walk Test” mode shall be a standard feature of the fire alarm control panel.  The walk 	test feature shall function so that each alarm input tested will operate the associated 	notification appliance for two seconds.  The FACP will then automatically perform a reset 	and confirm normal device operation.  The event memory shall contain the information on 	the point tested. the zone tripped, the zone restore and the individual points return to normal.

A “Fire Drill” mode shall allow the manual testing of the fire alarm system notification circuits.  The “Fire Drill” shall be capable of being controlled at the main annunciator, remote annunciators and via a remote contact input.

A “Bypass Mode” shall allow for any point or notification circuit to be bypassed without effecting the operation of the total fire system.

#### 2.1.17	Remote Input Capabilities

The control panel shall have provisions for supervised switch inputs for the purpose of Alarm reset and Alarm/Trouble restore.

#### 2.1.18	Notification Appliance Mapping Structure

All notification circuits and modules shall be programmable via a mapping structure that allows for a maximum of 999 output groups.  Each of these groups shall have the ability to be triggered by any of the panels 999 Zones.  A zone may trigger from groups individually, or may contain a global trigger for manual pull stations, fire drills and two different system alarms.  Additionally each Zone will individually control the cadence pattern of each of the Groups that it is “Mapped” to so that sounders can indicate a variety of conditions.  The Zone shall be capable of issuing a different cadence pattern for each of the Groups under it’s control.  The mapping structure must also allow a group to be designated to “ignore cadence” for use with strobes and other continuous input devices. Zones shall have eight different output categories; Detector alarm, Trouble, Supervisory, Pre-alarm, Waterflow, Manual pull, Zone Auxiliary one and Zone Auxiliary two. The patterns are; March code, ANSI 3.41, Single Stroke Bell Temporal, California code, Zone 1 coded, Zone 2 coded, Zone 3 coded, Zone 4 coded, Zone 5 coded, Zone 6 coded, Zone 7 coded, Zone 8 coded, Custom output pattern 1, Custom output pattern 2, Custom output pattern 3, Custom output pattern 4, and Constant.

#### 2.1.19	Downloading Software

The fire alarm control panel must support up/downloading of system programming from a Windows based PC.  The FACP must also be able to download the detector sensitivity test results and a 1000 event system event buffer to the PC. Communication shall take place over a direct connection to the PC and/or via the same telephone lines as the built in digital communicator and shall not require an external modem to be connected to the panel.  The downloading software shall contain a code that will block unauthorized persons from accessing the panel via direct connection or over the phone lines.

#### 2.1.20	English language descriptions

The FACP shall provide the ability to have a text description of each system device, input zone and output group on the system.  The use of individual lights to provide descriptions will not be acceptable.

### 2.2	SYSTEM OPERATION

#### 2.2.1	Alarm

When a device indicates any alarm condition the control panel must respond within 10 seconds.  The General Alarm or Supervisory Alarm LED on the annunciator(s) should light and the LCD should prompt the user as to the number of current events.  The alarm information must be stored in event memory for later review.  Event memory must be available at the main and all remote annunciators.

When the alarmed device is restored to normal, the control panel shall be required to be manually reset to clear the alarm condition, except that the alarms may be silenced as programmed.

An alarm shall be silenced by a code at the main or remote annunciators.  When silenced, this shall not prevent the resounding of subsequent events if another event should occur (subsequent alarm feature).  When alarms are silenced the silenced LED on the control panel, and on any remote annunciators shall remain lit, until the alarmed device is returned to normal

#### 2.2.2	Troubles

When a device indicates a trouble condition, the control panel System Trouble LED should light and the LCD should prompt the user as to the number of current events.  The trouble 	information must be stored in event memory for later review.  Event memory must be available at the main and all remote annunciators.

When the device in trouble is restored to normal, the control panel shall be automatically reset; the trouble restore information must be stored in event memory for later review.  Event memory must be available at the main and all remote annunciators.  A trouble shall be silenced by a code or at the main or remote annunciators.  When silenced, this shall not prevent the resounding of subsequent events if another event should occur.

#### 2.2.3	Supervision methods

Each SLC loop shall be electrically supervised for opens and ground faults in the circuit wiring, and shall be so arranged that a fault condition on any loop will not cause an alarm to sound.  Additionally, every addressable device connected to the SLC will be supervised and individually identified if in a fault condition.  The occurrence of any fault will light a trouble LED and sound the system trouble sounder, but will not interfere with the proper operation of any circuit which does not have a fault condition.

Each indicating appliance circuit shall be electrically supervised for opens, grounds and short circuit faults, on the circuit wiring, and shall be so arranged that a fault condition on any indicating appliance circuit or group of circuits will not cause an alarm to sound. The occurrence of any fault will light the trouble LED and sound the system trouble sounder, but will not interfere with the proper operation of any circuit which does not have a fault condition.

## SECTION THREE: SYSTEM COMPONENTS

### 3.0	CONTROL UNIT

#### 3.1	System Cabinet

##### 3.1.1	Mounting

The system cabinet shall be red and can be either surface or flush mounted.  The cabinet door shall be easily removable to facilitate installation and service.

##### 3.1.2	Audible System Trouble Sounder

An audible system trouble sounder shall be an integral part of the control unit. Provisions shall also be provided for an optional supervised remote trouble signal.

#### 3.2	Power Supply and Charger:

The entire system shall operate on 24 VDC, filtered switch mode power supply with the 		rated current available of 9 Amps. The FACP must have a battery charging circuit 		capable of complying with the following requirements:

Sixty (60) hours of battery standby with five (5) minutes of alarm signaling at the 			end of this sixty (60) hour period (as required per NFPA 72 remote station 				signaling requirements) using rechargeable batteries with automatic charger to 				maintain standby gel-cell batteries in a fully charged condition.

OR

Twenty-four (24) hours of battery standby with five (5) minutes of alarm signaling at the end of this twenty-four (24) hour period (as required per NFPA 72 central station signaling requirements) using rechargeable batteries with automatic charger to maintain gel-cell batteries in a fully charged condition.

The power supply shall comply with U.L. Standard 864 for power limiting.

The FACP will indicate a trouble condition if there is a loss of AC power or if the batteries are missing or of insufficient capacity to support proper system operation in the event of AC failure.  A “Battery Test” will be performed automatically every minute to check the integrity of the batteries.  The test must disconnect the batteries from the charging circuit and place a load on the battery to verify the battery condition.

##### 3.2.1	Connections and Circuits

Connections to the light and power service shall be on a dedicated branch circuit in accordance with the National Fire Alarm Code NFPA 72, National Electrical Code (NEC) NFPA 70, and the local authority having jurisdiction (AHJ).

The circuit and connections shall be mechanically protected.

A circuit disconnecting means shall be accessible only to authorized personnel and shall be clearly marked “FIRE ALARM CIRCUIT CONTROL”.

## SECTION FOUR:  ACCESSORY COMPONENTS

### 4.1	The FACP shall support the following devices on the RS-485 data bus:

5815XL	            Signaling Line Circuit Expander (SLC) Module

5824		            Printer Interface Module

SCSS-700ANN             LCD Remote Annunciator

5865-3	            LED Remote Annunciator

5865-4	            LED Remote Annunciator with reset and silence switches

5880 	            LED I/O module

5496                              Remote Addressable Power Supply 6.0 Amp

### 4.2	The FACP shall support the operation of 159 detectors and 159 addressable module total devices per SLC loop without regard to device type.  The following devices shall be supported:

SD355 		             Addressable Photoelectric Smoke detector

SD355T	             Addressable Photoelectric Smoke detector with Thermal

H355		             Addressable Heat Sensor

H355R		             Addressable Heat with Rate of Rise

H355HT	             Addressable Heat High temp 190°

D355PL		Addressable Photoelectric duct Detector does include SD355R head

B350LP 		6” detector base

CRF-300		Addressable Relay Module

CRF-300-6		Addressable Multi Relay Module

MMF-300		Addressable Input Module (Class A or B)

MMF-301		Mini Input Module

MDF-300		Addressable Dual Input Module

MMF-300-10      	Addressable Multi Input Module (10)

CMF-300		Addressable Control Module

`	CMF-300-6		Addressable Control Multi Module (6)

MMF-302		Two Wire Smoke Detector Module

MMF-302-6		6 Multi Smoke Detector Module

I300			Isolation Module

BEAM355		Addressable Beam Detector

BEAM355-S		Addressable Beam Detector with Test feature

B224RB		Detector Relay Base

B200SR		Detector Sounder Base

RTS151KEY		Remote Test Switch For Photoelectric Duct Detector

BG-12LX		Addressable Dual Action Pull Station

The FACP shall support these other Fire-Lite devices via addressable input, addressable

Notification or Addressable Output Modules.

  - Furnish and install, where shown on the drawings, the following devices

    - Manual Fire Alarm Stations

Manual Fire Alarm Stations shall be non-coded, break glass, single or double action type, with a key operated test-reset lock in order that they may be tested, and so designed that after actual emergency operation, they cannot be restored to normal except by use of a key. The reset key shall be so designed that it will reset manual station and open FACP without use of another key. An operated station shall automatically condition itself so as to be visually detected, as operated, at a minimum distance of fifty feet, front or side. Stations shall be suitable for surface mounting on matching backbox, or semi-flush mounting on a standard single-gang box, and shall be installed within the limits defined by the Americans with Disabilities Act (ADA) dependent on manual station accessibility or per local requirements. Manual stations shall be Model BG-12LX.  If using conventional pull stations they must be installed in conjunction with an Addressable Input Module (MMF-300) or Mini Input Module (MMF-301) used with the manual stations.  Shall be Fire-Lite Models BG-12, BG-12L, BG-12S, or BG-12SL and Underwriters Laboratories listed when used with addressable modules.

    - Remote Power Supplies

The Remote Power Supplies for Notification appliances shall be the Model 5496. The Model 5496 Intelligent Power Supply shall be connected to the main S-Bus and be programmed through the SCSS-700 control. It will support 6 amps of 24 volt DC power, with 4 Flexput circuits, rated at 3 amps each.  The power supply will also regenerate the S-Bus for an additional 6000’.

  - Notification Devices

The visual and audio/visual signaling devices shall be compatible with the SCSS-700, SCSS-00ND, or 5496 as stated in the installation manuals and be Listed with Underwriters Laboratories Inc. per UL 1971 and/or 1638. Each indicating appliance circuit shall be electrically supervised for opens, grounds and short circuit faults, on the circuit wiring, and shall be so arranged that a fault condition on any indicating appliance circuit or group of circuits will not cause an alarm to sound. The occurrence of any fault will light the trouble LED and sound the system trouble sounder, but will not interfere with the proper operation of any circuit which does not have a fault condition. The notification appliance (combination audio/visual units only) shall produce a peak sound output of 90dba or greater as measured in an anechoic chamber. The appliance shall be capable of meeting the candela requirements of the blueprints presented by the Engineer and ADA.  The appliance shall be polarized to allow for electrical supervision of the system wiring.  The unit shall be provided with terminals with barriers for input/output wiring and be able to mount a single gang or double gang box or double workbox with the use of an adapter plate.  The unit shall have an input voltage range of 19-30 volts

4.5	Smoke Detectors

Smoke detectors shall be Fire-Lite Model SD355 ceiling mounted Analog/Addressable photoelectric smoke detectors. The combination detector head and twist lock base shall be U.L. listed compatible with the Stanley SCSS-700 fire alarm control panel.

The base shall permit direct interchange with Fire-Lite’s SD355 smoke detector or the H355 detector. The base shall be the appropriate twist lock base B350LP.

The smoke detector shall have a flashing status LED for visual supervision. When the detector is actuated, the flashing LED will latch on steady at full brilliance. The detector may be reset by actuating the control panel’s reset switch. The sensitivity of the detector shall be capable of being selected and measured by the control panel without the need for external test equipment.

The vandal security-locking feature shall be used in those areas as indicated on the drawing. The locking feature shall be field selectable when required. It shall be possible to perform a sensitivity test of the detector without the need of generating smoke. The test method shall simulate the effects of products of combustion in the chamber to ensure testing of the detector circuits.

Detectors shall have completely closed back to restrict entry of dust and air turbulence and have a 30 mesh insect screen. Electronics of the unit shall be shielded to protect against false alarms from E.M.I. and R.F.I.

  - Heat Detectors

Furnish and install analog/addressable heat detectors, Fire-Lite Model H355. The combination heat detector and twist lock base shall be U.L. listed compatible with the Stanley SCSS-700 fire alarm control panel.

The base shall permit direct interchange with the Fire-Lite Model SD355 photoelectric smoke detector. The base shall be appropriate twist lock base B350LP.

The heat detector shall have a flashing status LED for visual supervision. When the detector is actuated, the flashing LED will latch on steady at full brilliance. The detector may be reset by actuating the control panel’s reset switch. The vandal security-locking feature shall be used in those areas as indicated on the drawings. Electronics of the unit shall be shielded to protect against false alarms from E.M.I. and R.F.I.

  - Duct Detectors

Duct Detector shall be Fire-Lite Model D355PL with an SD355R smoke head.

## SECTION FIVE: WIRING

### 5.1	Installer’s Responsibilities

The installer shall coordinate the installation of the fire alarm equipment.

All conductors and wiring shall be installed according to the manufacturer’s 			recommendations.

It shall be the installer’s responsibility to coordinate with the supplier, regarding the 		correct wiring procedures before installing any conduits or conductors.

#### 5.2	Installation of System Components

System components shall be installed in accordance with the latest revisions of the 		appropriate NFPA pamphlets, the requirements contained herein, National Electrical 		Code, local and state regulations, the requirements of the fire department and other 		applicable authorities having jurisdiction (AHJ).

All wire used on the fire alarm system shall be U.L. Listed as fire alarm protection 		signaling circuit cable per National Electrical Code, Articles 760.

SECTION SIX: WARRANTY AND FINAL TEST

### 6.1	General

The contractor shall warrant all equipment and wiring free from inherent mechanical and electrical defects for one year (365 days) from the date of final acceptance.

#### 6.2	Final Test

Before the installation shall be considered completed and acceptable by the awarding 		authority, a test of the system shall be performed as follows:

The contractor’s job foreman, a representative of the owner, and the fire 				department shall operate every building fire alarm device to ensure proper 			operation and correct annunciation at the control panel.

At least one half of all tests shall be performed on battery standby power.

Where application of heat would destroy any detector, it may be manually 			activated.

The communication loops and the indicating appliance circuits shall be opened in at least two (2) locations per circuit to check for the presence of correct supervision circuitry.

When the testing has been completed to the satisfaction of both the contractor’s job foreman and owner, a notarized letter cosigned by each attesting to the satisfactory completion of said testing shall be forwarded to the owner and the fire department.

The contractor shall leave the fire alarm system in proper working order, and, without additional expense to the owner, shall replace any defective materials or equipment provided by him under this contract within one year (365 days) from the date of final acceptance by the awarding authority.

Prior to final test the fire department must be notified in accordance with local requirements.

### 6.3	As-Built Drawings, Testing, and Maintenance Instructions

#### 6.3.1	As-Built Drawings

A complete set of reproducible “as-built” drawings showing installed wiring, color coding, and wire tag notations for exact locations of all installed equipment, specific interconnections between all equipment, and internal wiring of the equipment shall be delivered to the owner upon completion of system.

##### 6.3.2	Operating and Instruction Manuals

Operating and instruction manuals shall be submitted prior to testing of the system. Three (3) complete sets of operating and instruction manuals shall be delivered to the owner upon completion.  User operating instructions shall be provided prominently displayed on a separate sheet located next to the control unit in accordance with U.L. Standard 864.